## README
Modbus RTU
Modbus RTU exchanges of the project, the PLC is master.
Sheets:
LINES : one row per serial line (COM port settings, shared by every slave of the line)
SLAVES : one row per instance on Modbus RTU (line, slave device, address)
<instance> : one sheet per instance, one row per coil or register, with its GVL_MODBUS and GVL_COM variables
Rules:
The register map comes from the TYPE file. This file adds what belongs to the instance : variables and channel settings.
A 32-bit value uses 2 rows (Word = MSW / LSW).
Sheet name = instance name, as in SLAVES.
Cells marked "TO CHECK" (yellow) are values not confirmed yet.

## LINES
Line | CODESYS COM port device | CODESYS master device | PLC port | PLC role | Baud rate | Parity | Data bits | Stop bits | Response timeout (ms) | Comment
RTU_1 | Modbus_COM_Port | Modbus_Client_COM_Port | TO CHECK | Master | 9600 | TO CHECK | TO CHECK | TO CHECK | TO CHECK
Note on A1: Name of the serial line (RTU_1, RTU_2...). One line = one COM port, every slave of the line has the same speed and format.
Note on B1: Name of the Modbus COM device in the CODESYS device tree (e.g. Modbus_COM_Port).
Note on C1: Name of the Modbus master (client) device under the COM port in the CODESYS device tree.
Note on D1: Serial port of the P2CDS-622 used by the line.
Note on E1: Role of the PLC on the line.
Note on F1: Line speed, same on the PLC port and on every slave.
Note on G1: Parity of the serial frame, same on every slave.
Note on H1: Data bits of the serial frame.
Note on I1: Stop bits of the serial frame.
Note on J1: Time the master waits for a slave answer before an error.
Note on K1: Free text. Not used by the generator.

## SLAVES
Instance | Object type | Line | CODESYS slave device | Slave address | 32-bit word order | Comment
ADM100W_1 | ADM100W | RTU_1 | ADM100 | TO CHECK | ABCD (MSW first)
DIP1500_1 | DIP1500 | RTU_1 | Kamoer_DIP1500 | 11 | CDAB (LSW first)
Note on A1: Instance name (e.g. DIP1500_1). Must exist in the program : GVL_COM.COM_<instance>, GVL_EXC.EXC_<instance>... <INSTANCE> in a TYPE file template = placeholder.
Note on B1: Type of the instance = name of its TYPE file (TYPE_<type>.xlsx).
Note on C1: Name of the serial line (RTU_1, RTU_2...). One line = one COM port, every slave of the line has the same speed and format.
Note on D1: Name of the Modbus slave device in the CODESYS device tree (under the master).
Note on E1: Modbus address of the equipment (1..247), set on the equipment itself.
Note on F1: Order of the 2 words of 32-bit values for this equipment.
Note on G1: Free text. Not used by the generator.

## ADM100W_1
Table | Equipment address | Channel offset | Function | Direction | Name | Type | Word | Scale | Unit | GVL_MODBUS variable | GVL_COM variable | CODESYS channel | Comment
Coil | 0 | 0 | FC01 Read Coils | Equipment to PLC | ADM100W Alarm 1 Status | BOOL |  |  |  | GVL_MODBUS.ADM100W_Alarms[0].0 | GVL_COM.COM_ADM100W_1.COM_INPUT_COILS[0].0 | Read, cyclic
Coil | 1 | 1 | FC01 Read Coils | Equipment to PLC | ADM100W Alarm 2 Status | BOOL |  |  |  | GVL_MODBUS.ADM100W_Alarms[0].1 | GVL_COM.COM_ADM100W_1.COM_INPUT_COILS[0].1 | Read, cyclic
Coil | 2 | 2 | FC01 Read Coils | Equipment to PLC | ADM100W Alarm 3 Status | BOOL |  |  |  | GVL_MODBUS.ADM100W_Alarms[0].2 | GVL_COM.COM_ADM100W_1.COM_INPUT_COILS[0].2 | Read, cyclic
Coil | 3 | 3 | FC01 Read Coils | Equipment to PLC | ADM100W Alarm 4 Status | BOOL |  |  |  | GVL_MODBUS.ADM100W_Alarms[0].3 | GVL_COM.COM_ADM100W_1.COM_INPUT_COILS[0].3 | Read, cyclic
Coil | 4 | 4 | FC01 Read Coils | Equipment to PLC | ADM100W Alarm 5 Status | BOOL |  |  |  | GVL_MODBUS.ADM100W_Alarms[0].4 | GVL_COM.COM_ADM100W_1.COM_INPUT_COILS[0].4 | Read, cyclic
Coil | 5 | 5 | FC01 Read Coils | Equipment to PLC | ADM100W Alarm 6 Status | BOOL |  |  |  | GVL_MODBUS.ADM100W_Alarms[0].5 | GVL_COM.COM_ADM100W_1.COM_INPUT_COILS[0].5 | Read, cyclic
Coil | 6 | 6 | FC01 Read Coils | Equipment to PLC | ADM100W Alarm 7 Status | BOOL |  |  |  | GVL_MODBUS.ADM100W_Alarms[0].6 | GVL_COM.COM_ADM100W_1.COM_INPUT_COILS[0].6 | Read, cyclic
Coil | 7 | 7 | FC01 Read Coils | Equipment to PLC | ADM100W Alarm 8 Status | BOOL |  |  |  | GVL_MODBUS.ADM100W_Alarms[0].7 | GVL_COM.COM_ADM100W_1.COM_INPUT_COILS[0].7 | Read, cyclic
Coil | 8 | 8 | FC01 Read Coils | Equipment to PLC | ADM100W Alarm 9 Status | BOOL |  |  |  | GVL_MODBUS.ADM100W_Alarms[1].0 | GVL_COM.COM_ADM100W_1.COM_INPUT_COILS[1].0 | Read, cyclic
Coil | 9 | 9 | FC01 Read Coils | Equipment to PLC | ADM100W Alarm 10 Status | BOOL |  |  |  | GVL_MODBUS.ADM100W_Alarms[1].1 | GVL_COM.COM_ADM100W_1.COM_INPUT_COILS[1].1 | Read, cyclic
IR | 0 | 0 | FC04 Read Input Registers | Equipment to PLC | ADM100W Frequency | REAL | MSW | 1 | Hz | GVL_MODBUS.ADM100W_InputRegisters[0] | GVL_COM.COM_ADM100W_1.COM_INPUT_IR[0] | Read, cyclic
IR | 1 | 1 | FC04 Read Input Registers | Equipment to PLC | ADM100W Frequency | REAL | LSW | 1 | Hz | GVL_MODBUS.ADM100W_InputRegisters[1] | GVL_COM.COM_ADM100W_1.COM_INPUT_IR[1] | Read, cyclic
IR | 2 | 2 | FC04 Read Input Registers | Equipment to PLC | ADM100W L1-L2 Voltage | REAL | MSW | 1 | V | GVL_MODBUS.ADM100W_InputRegisters[2] | GVL_COM.COM_ADM100W_1.COM_INPUT_IR[2] | Read, cyclic
IR | 3 | 3 | FC04 Read Input Registers | Equipment to PLC | ADM100W L1-L2 Voltage | REAL | LSW | 1 | V | GVL_MODBUS.ADM100W_InputRegisters[3] | GVL_COM.COM_ADM100W_1.COM_INPUT_IR[3] | Read, cyclic
IR | 4 | 4 | FC04 Read Input Registers | Equipment to PLC | ADM100W L1-N Voltage | REAL | MSW | 1 | V | GVL_MODBUS.ADM100W_InputRegisters[4] | GVL_COM.COM_ADM100W_1.COM_INPUT_IR[4] | Read, cyclic
IR | 5 | 5 | FC04 Read Input Registers | Equipment to PLC | ADM100W L1-N Voltage | REAL | LSW | 1 | V | GVL_MODBUS.ADM100W_InputRegisters[5] | GVL_COM.COM_ADM100W_1.COM_INPUT_IR[5] | Read, cyclic
IR | 6 | 6 | FC04 Read Input Registers | Equipment to PLC | ADM100W L1 Current | REAL | MSW | 1 | A | GVL_MODBUS.ADM100W_InputRegisters[6] | GVL_COM.COM_ADM100W_1.COM_INPUT_IR[6] | Read, cyclic
IR | 7 | 7 | FC04 Read Input Registers | Equipment to PLC | ADM100W L1 Current | REAL | LSW | 1 | A | GVL_MODBUS.ADM100W_InputRegisters[7] | GVL_COM.COM_ADM100W_1.COM_INPUT_IR[7] | Read, cyclic
IR | 8 | 8 | FC04 Read Input Registers | Equipment to PLC | ADM100W L1 Active Power | REAL | MSW | 1 | per ADM100W config | GVL_MODBUS.ADM100W_InputRegisters[8] | GVL_COM.COM_ADM100W_1.COM_INPUT_IR[8] | Read, cyclic
IR | 9 | 9 | FC04 Read Input Registers | Equipment to PLC | ADM100W L1 Active Power | REAL | LSW | 1 | per ADM100W config | GVL_MODBUS.ADM100W_InputRegisters[9] | GVL_COM.COM_ADM100W_1.COM_INPUT_IR[9] | Read, cyclic
IR | 10 | 10 | FC04 Read Input Registers | Equipment to PLC | ADM100W L1 Apparent Power | REAL | MSW | 1 | per ADM100W config | GVL_MODBUS.ADM100W_InputRegisters[10] | GVL_COM.COM_ADM100W_1.COM_INPUT_IR[10] | Read, cyclic
IR | 11 | 11 | FC04 Read Input Registers | Equipment to PLC | ADM100W L1 Apparent Power | REAL | LSW | 1 | per ADM100W config | GVL_MODBUS.ADM100W_InputRegisters[11] | GVL_COM.COM_ADM100W_1.COM_INPUT_IR[11] | Read, cyclic
IR | 12 | 12 | FC04 Read Input Registers | Equipment to PLC | ADM100W L1 Reactive Power | REAL | MSW | 1 | per ADM100W config | GVL_MODBUS.ADM100W_InputRegisters[12] | GVL_COM.COM_ADM100W_1.COM_INPUT_IR[12] | Read, cyclic
IR | 13 | 13 | FC04 Read Input Registers | Equipment to PLC | ADM100W L1 Reactive Power | REAL | LSW | 1 | per ADM100W config | GVL_MODBUS.ADM100W_InputRegisters[13] | GVL_COM.COM_ADM100W_1.COM_INPUT_IR[13] | Read, cyclic
IR | 14 | 14 | FC04 Read Input Registers | Equipment to PLC | ADM100W L1 Current Phase Angle | REAL | MSW | 1 | ° | GVL_MODBUS.ADM100W_InputRegisters[14] | GVL_COM.COM_ADM100W_1.COM_INPUT_IR[14] | Read, cyclic
IR | 15 | 15 | FC04 Read Input Registers | Equipment to PLC | ADM100W L1 Current Phase Angle | REAL | LSW | 1 | ° | GVL_MODBUS.ADM100W_InputRegisters[15] | GVL_COM.COM_ADM100W_1.COM_INPUT_IR[15] | Read, cyclic
IR | 16 | 16 | FC04 Read Input Registers | Equipment to PLC | ADM100W L1 Power Factor | REAL | MSW | 1 |  | GVL_MODBUS.ADM100W_InputRegisters[16] | GVL_COM.COM_ADM100W_1.COM_INPUT_IR[16] | Read, cyclic
IR | 17 | 17 | FC04 Read Input Registers | Equipment to PLC | ADM100W L1 Power Factor | REAL | LSW | 1 |  | GVL_MODBUS.ADM100W_InputRegisters[17] | GVL_COM.COM_ADM100W_1.COM_INPUT_IR[17] | Read, cyclic
IR | 18 | 18 | FC04 Read Input Registers | Equipment to PLC | ADM100W L1 Voltage THD | REAL | MSW | 1 | % | GVL_MODBUS.ADM100W_InputRegisters[18] | GVL_COM.COM_ADM100W_1.COM_INPUT_IR[18] | Read, cyclic
IR | 19 | 19 | FC04 Read Input Registers | Equipment to PLC | ADM100W L1 Voltage THD | REAL | LSW | 1 | % | GVL_MODBUS.ADM100W_InputRegisters[19] | GVL_COM.COM_ADM100W_1.COM_INPUT_IR[19] | Read, cyclic
IR | 20 | 20 | FC04 Read Input Registers | Equipment to PLC | ADM100W L1 Current THD | REAL | MSW | 1 | % | GVL_MODBUS.ADM100W_InputRegisters[20] | GVL_COM.COM_ADM100W_1.COM_INPUT_IR[20] | Read, cyclic
IR | 21 | 21 | FC04 Read Input Registers | Equipment to PLC | ADM100W L1 Current THD | REAL | LSW | 1 | % | GVL_MODBUS.ADM100W_InputRegisters[21] | GVL_COM.COM_ADM100W_1.COM_INPUT_IR[21] | Read, cyclic
IR | 22 | 22 | FC04 Read Input Registers | Equipment to PLC | ADM100W L1 Max Load | REAL | MSW | 1 | per ADM100W config | GVL_MODBUS.ADM100W_InputRegisters[22] | GVL_COM.COM_ADM100W_1.COM_INPUT_IR[22] | Read, cyclic
IR | 23 | 23 | FC04 Read Input Registers | Equipment to PLC | ADM100W L1 Max Load | REAL | LSW | 1 | per ADM100W config | GVL_MODBUS.ADM100W_InputRegisters[23] | GVL_COM.COM_ADM100W_1.COM_INPUT_IR[23] | Read, cyclic
IR | 24 | 24 | FC04 Read Input Registers | Equipment to PLC | ADM100W L1-L2 Voltage Phase Angle | REAL | MSW | 1 | ° | GVL_MODBUS.ADM100W_InputRegisters[24] | GVL_COM.COM_ADM100W_1.COM_INPUT_IR[24] | Read, cyclic
IR | 25 | 25 | FC04 Read Input Registers | Equipment to PLC | ADM100W L1-L2 Voltage Phase Angle | REAL | LSW | 1 | ° | GVL_MODBUS.ADM100W_InputRegisters[25] | GVL_COM.COM_ADM100W_1.COM_INPUT_IR[25] | Read, cyclic
IR | 26 | 26 | FC04 Read Input Registers | Equipment to PLC | ADM100W L2-L3 Voltage | REAL | MSW | 1 | V | GVL_MODBUS.ADM100W_InputRegisters[26] | GVL_COM.COM_ADM100W_1.COM_INPUT_IR[26] | Read, cyclic
IR | 27 | 27 | FC04 Read Input Registers | Equipment to PLC | ADM100W L2-L3 Voltage | REAL | LSW | 1 | V | GVL_MODBUS.ADM100W_InputRegisters[27] | GVL_COM.COM_ADM100W_1.COM_INPUT_IR[27] | Read, cyclic
IR | 28 | 28 | FC04 Read Input Registers | Equipment to PLC | ADM100W L2-N Voltage | REAL | MSW | 1 | V | GVL_MODBUS.ADM100W_InputRegisters[28] | GVL_COM.COM_ADM100W_1.COM_INPUT_IR[28] | Read, cyclic
IR | 29 | 29 | FC04 Read Input Registers | Equipment to PLC | ADM100W L2-N Voltage | REAL | LSW | 1 | V | GVL_MODBUS.ADM100W_InputRegisters[29] | GVL_COM.COM_ADM100W_1.COM_INPUT_IR[29] | Read, cyclic
IR | 30 | 30 | FC04 Read Input Registers | Equipment to PLC | ADM100W L2 Current | REAL | MSW | 1 | A | GVL_MODBUS.ADM100W_InputRegisters[30] | GVL_COM.COM_ADM100W_1.COM_INPUT_IR[30] | Read, cyclic
IR | 31 | 31 | FC04 Read Input Registers | Equipment to PLC | ADM100W L2 Current | REAL | LSW | 1 | A | GVL_MODBUS.ADM100W_InputRegisters[31] | GVL_COM.COM_ADM100W_1.COM_INPUT_IR[31] | Read, cyclic
IR | 32 | 32 | FC04 Read Input Registers | Equipment to PLC | ADM100W L2 Active Power | REAL | MSW | 1 | per ADM100W config | GVL_MODBUS.ADM100W_InputRegisters[32] | GVL_COM.COM_ADM100W_1.COM_INPUT_IR[32] | Read, cyclic
IR | 33 | 33 | FC04 Read Input Registers | Equipment to PLC | ADM100W L2 Active Power | REAL | LSW | 1 | per ADM100W config | GVL_MODBUS.ADM100W_InputRegisters[33] | GVL_COM.COM_ADM100W_1.COM_INPUT_IR[33] | Read, cyclic
IR | 34 | 34 | FC04 Read Input Registers | Equipment to PLC | ADM100W L2 Apparent Power | REAL | MSW | 1 | per ADM100W config | GVL_MODBUS.ADM100W_InputRegisters[34] | GVL_COM.COM_ADM100W_1.COM_INPUT_IR[34] | Read, cyclic
IR | 35 | 35 | FC04 Read Input Registers | Equipment to PLC | ADM100W L2 Apparent Power | REAL | LSW | 1 | per ADM100W config | GVL_MODBUS.ADM100W_InputRegisters[35] | GVL_COM.COM_ADM100W_1.COM_INPUT_IR[35] | Read, cyclic
IR | 36 | 36 | FC04 Read Input Registers | Equipment to PLC | ADM100W L2 Reactive Power | REAL | MSW | 1 | per ADM100W config | GVL_MODBUS.ADM100W_InputRegisters[36] | GVL_COM.COM_ADM100W_1.COM_INPUT_IR[36] | Read, cyclic
IR | 37 | 37 | FC04 Read Input Registers | Equipment to PLC | ADM100W L2 Reactive Power | REAL | LSW | 1 | per ADM100W config | GVL_MODBUS.ADM100W_InputRegisters[37] | GVL_COM.COM_ADM100W_1.COM_INPUT_IR[37] | Read, cyclic
IR | 38 | 38 | FC04 Read Input Registers | Equipment to PLC | ADM100W L2 Current Phase Angle | REAL | MSW | 1 | ° | GVL_MODBUS.ADM100W_InputRegisters[38] | GVL_COM.COM_ADM100W_1.COM_INPUT_IR[38] | Read, cyclic
IR | 39 | 39 | FC04 Read Input Registers | Equipment to PLC | ADM100W L2 Current Phase Angle | REAL | LSW | 1 | ° | GVL_MODBUS.ADM100W_InputRegisters[39] | GVL_COM.COM_ADM100W_1.COM_INPUT_IR[39] | Read, cyclic
IR | 40 | 40 | FC04 Read Input Registers | Equipment to PLC | ADM100W L2 Power Factor | REAL | MSW | 1 |  | GVL_MODBUS.ADM100W_InputRegisters[40] | GVL_COM.COM_ADM100W_1.COM_INPUT_IR[40] | Read, cyclic
IR | 41 | 41 | FC04 Read Input Registers | Equipment to PLC | ADM100W L2 Power Factor | REAL | LSW | 1 |  | GVL_MODBUS.ADM100W_InputRegisters[41] | GVL_COM.COM_ADM100W_1.COM_INPUT_IR[41] | Read, cyclic
IR | 42 | 42 | FC04 Read Input Registers | Equipment to PLC | ADM100W L2 Voltage THD | REAL | MSW | 1 | % | GVL_MODBUS.ADM100W_InputRegisters[42] | GVL_COM.COM_ADM100W_1.COM_INPUT_IR[42] | Read, cyclic
IR | 43 | 43 | FC04 Read Input Registers | Equipment to PLC | ADM100W L2 Voltage THD | REAL | LSW | 1 | % | GVL_MODBUS.ADM100W_InputRegisters[43] | GVL_COM.COM_ADM100W_1.COM_INPUT_IR[43] | Read, cyclic
IR | 44 | 44 | FC04 Read Input Registers | Equipment to PLC | ADM100W L2 Current THD | REAL | MSW | 1 | % | GVL_MODBUS.ADM100W_InputRegisters[44] | GVL_COM.COM_ADM100W_1.COM_INPUT_IR[44] | Read, cyclic
IR | 45 | 45 | FC04 Read Input Registers | Equipment to PLC | ADM100W L2 Current THD | REAL | LSW | 1 | % | GVL_MODBUS.ADM100W_InputRegisters[45] | GVL_COM.COM_ADM100W_1.COM_INPUT_IR[45] | Read, cyclic
IR | 46 | 46 | FC04 Read Input Registers | Equipment to PLC | ADM100W L2 Max Load | REAL | MSW | 1 | per ADM100W config | GVL_MODBUS.ADM100W_InputRegisters[46] | GVL_COM.COM_ADM100W_1.COM_INPUT_IR[46] | Read, cyclic
IR | 47 | 47 | FC04 Read Input Registers | Equipment to PLC | ADM100W L2 Max Load | REAL | LSW | 1 | per ADM100W config | GVL_MODBUS.ADM100W_InputRegisters[47] | GVL_COM.COM_ADM100W_1.COM_INPUT_IR[47] | Read, cyclic
IR | 48 | 48 | FC04 Read Input Registers | Equipment to PLC | ADM100W L1-L3 Voltage Phase Angle | REAL | MSW | 1 | ° | GVL_MODBUS.ADM100W_InputRegisters[48] | GVL_COM.COM_ADM100W_1.COM_INPUT_IR[48] | Read, cyclic
IR | 49 | 49 | FC04 Read Input Registers | Equipment to PLC | ADM100W L1-L3 Voltage Phase Angle | REAL | LSW | 1 | ° | GVL_MODBUS.ADM100W_InputRegisters[49] | GVL_COM.COM_ADM100W_1.COM_INPUT_IR[49] | Read, cyclic
IR | 50 | 50 | FC04 Read Input Registers | Equipment to PLC | ADM100W L3-L1 Voltage | REAL | MSW | 1 | V | GVL_MODBUS.ADM100W_InputRegisters[50] | GVL_COM.COM_ADM100W_1.COM_INPUT_IR[50] | Read, cyclic
IR | 51 | 51 | FC04 Read Input Registers | Equipment to PLC | ADM100W L3-L1 Voltage | REAL | LSW | 1 | V | GVL_MODBUS.ADM100W_InputRegisters[51] | GVL_COM.COM_ADM100W_1.COM_INPUT_IR[51] | Read, cyclic
IR | 52 | 52 | FC04 Read Input Registers | Equipment to PLC | ADM100W L3-N Voltage | REAL | MSW | 1 | V | GVL_MODBUS.ADM100W_InputRegisters[52] | GVL_COM.COM_ADM100W_1.COM_INPUT_IR[52] | Read, cyclic
IR | 53 | 53 | FC04 Read Input Registers | Equipment to PLC | ADM100W L3-N Voltage | REAL | LSW | 1 | V | GVL_MODBUS.ADM100W_InputRegisters[53] | GVL_COM.COM_ADM100W_1.COM_INPUT_IR[53] | Read, cyclic
IR | 54 | 54 | FC04 Read Input Registers | Equipment to PLC | ADM100W L3 Current | REAL | MSW | 1 | A | GVL_MODBUS.ADM100W_InputRegisters[54] | GVL_COM.COM_ADM100W_1.COM_INPUT_IR[54] | Read, cyclic
IR | 55 | 55 | FC04 Read Input Registers | Equipment to PLC | ADM100W L3 Current | REAL | LSW | 1 | A | GVL_MODBUS.ADM100W_InputRegisters[55] | GVL_COM.COM_ADM100W_1.COM_INPUT_IR[55] | Read, cyclic
IR | 56 | 56 | FC04 Read Input Registers | Equipment to PLC | ADM100W L3 Active Power | REAL | MSW | 1 | per ADM100W config | GVL_MODBUS.ADM100W_InputRegisters[56] | GVL_COM.COM_ADM100W_1.COM_INPUT_IR[56] | Read, cyclic
IR | 57 | 57 | FC04 Read Input Registers | Equipment to PLC | ADM100W L3 Active Power | REAL | LSW | 1 | per ADM100W config | GVL_MODBUS.ADM100W_InputRegisters[57] | GVL_COM.COM_ADM100W_1.COM_INPUT_IR[57] | Read, cyclic
IR | 58 | 58 | FC04 Read Input Registers | Equipment to PLC | ADM100W L3 Apparent Power | REAL | MSW | 1 | per ADM100W config | GVL_MODBUS.ADM100W_InputRegisters[58] | GVL_COM.COM_ADM100W_1.COM_INPUT_IR[58] | Read, cyclic
IR | 59 | 59 | FC04 Read Input Registers | Equipment to PLC | ADM100W L3 Apparent Power | REAL | LSW | 1 | per ADM100W config | GVL_MODBUS.ADM100W_InputRegisters[59] | GVL_COM.COM_ADM100W_1.COM_INPUT_IR[59] | Read, cyclic
IR | 60 | 60 | FC04 Read Input Registers | Equipment to PLC | ADM100W L3 Reactive Power | REAL | MSW | 1 | per ADM100W config | GVL_MODBUS.ADM100W_InputRegisters[60] | GVL_COM.COM_ADM100W_1.COM_INPUT_IR[60] | Read, cyclic
IR | 61 | 61 | FC04 Read Input Registers | Equipment to PLC | ADM100W L3 Reactive Power | REAL | LSW | 1 | per ADM100W config | GVL_MODBUS.ADM100W_InputRegisters[61] | GVL_COM.COM_ADM100W_1.COM_INPUT_IR[61] | Read, cyclic
IR | 62 | 62 | FC04 Read Input Registers | Equipment to PLC | ADM100W L3 Current Phase Angle | REAL | MSW | 1 | ° | GVL_MODBUS.ADM100W_InputRegisters[62] | GVL_COM.COM_ADM100W_1.COM_INPUT_IR[62] | Read, cyclic
IR | 63 | 63 | FC04 Read Input Registers | Equipment to PLC | ADM100W L3 Current Phase Angle | REAL | LSW | 1 | ° | GVL_MODBUS.ADM100W_InputRegisters[63] | GVL_COM.COM_ADM100W_1.COM_INPUT_IR[63] | Read, cyclic
IR | 64 | 64 | FC04 Read Input Registers | Equipment to PLC | ADM100W L3 Power Factor | REAL | MSW | 1 |  | GVL_MODBUS.ADM100W_InputRegisters[64] | GVL_COM.COM_ADM100W_1.COM_INPUT_IR[64] | Read, cyclic
IR | 65 | 65 | FC04 Read Input Registers | Equipment to PLC | ADM100W L3 Power Factor | REAL | LSW | 1 |  | GVL_MODBUS.ADM100W_InputRegisters[65] | GVL_COM.COM_ADM100W_1.COM_INPUT_IR[65] | Read, cyclic
IR | 66 | 66 | FC04 Read Input Registers | Equipment to PLC | ADM100W L3 Voltage THD | REAL | MSW | 1 | % | GVL_MODBUS.ADM100W_InputRegisters[66] | GVL_COM.COM_ADM100W_1.COM_INPUT_IR[66] | Read, cyclic
IR | 67 | 67 | FC04 Read Input Registers | Equipment to PLC | ADM100W L3 Voltage THD | REAL | LSW | 1 | % | GVL_MODBUS.ADM100W_InputRegisters[67] | GVL_COM.COM_ADM100W_1.COM_INPUT_IR[67] | Read, cyclic
IR | 68 | 68 | FC04 Read Input Registers | Equipment to PLC | ADM100W L3 Current THD | REAL | MSW | 1 | % | GVL_MODBUS.ADM100W_InputRegisters[68] | GVL_COM.COM_ADM100W_1.COM_INPUT_IR[68] | Read, cyclic
IR | 69 | 69 | FC04 Read Input Registers | Equipment to PLC | ADM100W L3 Current THD | REAL | LSW | 1 | % | GVL_MODBUS.ADM100W_InputRegisters[69] | GVL_COM.COM_ADM100W_1.COM_INPUT_IR[69] | Read, cyclic
IR | 70 | 70 | FC04 Read Input Registers | Equipment to PLC | ADM100W L3 Max Load | REAL | MSW | 1 | per ADM100W config | GVL_MODBUS.ADM100W_InputRegisters[70] | GVL_COM.COM_ADM100W_1.COM_INPUT_IR[70] | Read, cyclic
IR | 71 | 71 | FC04 Read Input Registers | Equipment to PLC | ADM100W L3 Max Load | REAL | LSW | 1 | per ADM100W config | GVL_MODBUS.ADM100W_InputRegisters[71] | GVL_COM.COM_ADM100W_1.COM_INPUT_IR[71] | Read, cyclic
IR | 72 | 72 | FC04 Read Input Registers | Equipment to PLC | ADM100W Internal Temperature | REAL | MSW | 1 | per ADM100W config | GVL_MODBUS.ADM100W_InputRegisters[72] | GVL_COM.COM_ADM100W_1.COM_INPUT_IR[72] | Read, cyclic
IR | 73 | 73 | FC04 Read Input Registers | Equipment to PLC | ADM100W Internal Temperature | REAL | LSW | 1 | per ADM100W config | GVL_MODBUS.ADM100W_InputRegisters[73] | GVL_COM.COM_ADM100W_1.COM_INPUT_IR[73] | Read, cyclic
IR | 74 | 74 | FC04 Read Input Registers | Equipment to PLC | ADM100W Active Energy | REAL | MSW | 1 | per ADM100W config | GVL_MODBUS.ADM100W_InputRegisters[74] | GVL_COM.COM_ADM100W_1.COM_INPUT_IR[74] | Read, cyclic
IR | 75 | 75 | FC04 Read Input Registers | Equipment to PLC | ADM100W Active Energy | REAL | LSW | 1 | per ADM100W config | GVL_MODBUS.ADM100W_InputRegisters[75] | GVL_COM.COM_ADM100W_1.COM_INPUT_IR[75] | Read, cyclic
IR | 76 | 76 | FC04 Read Input Registers | Equipment to PLC | ADM100W Apparent Energy | REAL | MSW | 1 | per ADM100W config | GVL_MODBUS.ADM100W_InputRegisters[76] | GVL_COM.COM_ADM100W_1.COM_INPUT_IR[76] | Read, cyclic
IR | 77 | 77 | FC04 Read Input Registers | Equipment to PLC | ADM100W Apparent Energy | REAL | LSW | 1 | per ADM100W config | GVL_MODBUS.ADM100W_InputRegisters[77] | GVL_COM.COM_ADM100W_1.COM_INPUT_IR[77] | Read, cyclic
IR | 78 | 78 | FC04 Read Input Registers | Equipment to PLC | ADM100W Reactive Energy | REAL | MSW | 1 | per ADM100W config | GVL_MODBUS.ADM100W_InputRegisters[78] | GVL_COM.COM_ADM100W_1.COM_INPUT_IR[78] | Read, cyclic
IR | 79 | 79 | FC04 Read Input Registers | Equipment to PLC | ADM100W Reactive Energy | REAL | LSW | 1 | per ADM100W config | GVL_MODBUS.ADM100W_InputRegisters[79] | GVL_COM.COM_ADM100W_1.COM_INPUT_IR[79] | Read, cyclic
IR | 80 | 80 | FC04 Read Input Registers | Equipment to PLC | ADM100W Total Active Power | REAL | MSW | 1 | per ADM100W config | GVL_MODBUS.ADM100W_InputRegisters[80] | GVL_COM.COM_ADM100W_1.COM_INPUT_IR[80] | Read, cyclic
IR | 81 | 81 | FC04 Read Input Registers | Equipment to PLC | ADM100W Total Active Power | REAL | LSW | 1 | per ADM100W config | GVL_MODBUS.ADM100W_InputRegisters[81] | GVL_COM.COM_ADM100W_1.COM_INPUT_IR[81] | Read, cyclic
IR | 82 | 82 | FC04 Read Input Registers | Equipment to PLC | ADM100W Total Apparent Power | REAL | MSW | 1 | per ADM100W config | GVL_MODBUS.ADM100W_InputRegisters[82] | GVL_COM.COM_ADM100W_1.COM_INPUT_IR[82] | Read, cyclic
IR | 83 | 83 | FC04 Read Input Registers | Equipment to PLC | ADM100W Total Apparent Power | REAL | LSW | 1 | per ADM100W config | GVL_MODBUS.ADM100W_InputRegisters[83] | GVL_COM.COM_ADM100W_1.COM_INPUT_IR[83] | Read, cyclic
IR | 84 | 84 | FC04 Read Input Registers | Equipment to PLC | ADM100W Total Reactive Power | REAL | MSW | 1 | per ADM100W config | GVL_MODBUS.ADM100W_InputRegisters[84] | GVL_COM.COM_ADM100W_1.COM_INPUT_IR[84] | Read, cyclic
IR | 85 | 85 | FC04 Read Input Registers | Equipment to PLC | ADM100W Total Reactive Power | REAL | LSW | 1 | per ADM100W config | GVL_MODBUS.ADM100W_InputRegisters[85] | GVL_COM.COM_ADM100W_1.COM_INPUT_IR[85] | Read, cyclic
IR | 86 | 86 | FC04 Read Input Registers | Equipment to PLC | ADM100W All Phase Power Factor | REAL | MSW | 1 |  | GVL_MODBUS.ADM100W_InputRegisters[86] | GVL_COM.COM_ADM100W_1.COM_INPUT_IR[86] | Read, cyclic
IR | 87 | 87 | FC04 Read Input Registers | Equipment to PLC | ADM100W All Phase Power Factor | REAL | LSW | 1 |  | GVL_MODBUS.ADM100W_InputRegisters[87] | GVL_COM.COM_ADM100W_1.COM_INPUT_IR[87] | Read, cyclic
Note on A1: Modbus table : Coil, DI (discrete input), IR (input register), HR (holding register).
Note on B1: Register or coil address as written in the equipment manual (hex 0x4001 or decimal).
Note on C1: Position in the CODESYS Modbus channel and in the GVL_MODBUS array (0 = first register of the channel).
Note on D1: Modbus function code used by the CODESYS channel.
Note on E1: Equipment to PLC = read by the PLC. PLC to Equipment = written by the PLC.
Note on F1: Readable name of the value. Used as tag name in FUXA and as label in the supervisions.
Note on G1: Type of the value in the equipment. 32-bit values use 2 rows.
Note on H1: 32-bit value split in 2 registers : MSW = most significant word, LSW = least significant word. Empty for 16-bit and BOOL.
Note on I1: Conversion raw value -> engineering value, as written in the equipment manual. "1" = no conversion.
Note on J1: Engineering unit of the value (free text).
Note on K1: Element of GVL_MODBUS mapped in the CODESYS device I/O mapping (Modbus server or slave channel). GVL_MODBUS = exchange variables only.
Note on L1: Variable of GVL_COM copied to / from GVL_MODBUS by GFC_COM_IN / GFC_COM_OUT.
Note on M1: How the CODESYS Modbus master channel runs : cyclic, or on the rising edge of a trigger variable mapped in the slave I/O mapping.
Note on N1: Free text. Not used by the generator.

## DIP1500_1
Table | Equipment address | Channel offset | Function | Direction | Name | Type | Word | Scale | Unit | GVL_MODBUS variable | GVL_COM variable | CODESYS channel | Comment
Coil | 0x0001 | 0 | FC15 Write Multiple Coils | PLC to Equipment | DIP1500 Motor Start Stop | BOOL |  |  |  | GVL_MODBUS.DIP1500_Coils[0] | GVL_COM.COM_DIP1500_1.COM_OUTPUT_COILS[0] | TO CHECK | Write channel mode not confirmed (cyclic or trigger)
Coil | 0x0002 | 1 | FC15 Write Multiple Coils | PLC to Equipment | DIP1500 Motor Direction | BOOL |  |  |  | GVL_MODBUS.DIP1500_Coils[1] | GVL_COM.COM_DIP1500_1.COM_OUTPUT_COILS[1] | TO CHECK | Write channel mode not confirmed (cyclic or trigger)
Coil | 0x0003 | 2 | FC15 Write Multiple Coils | PLC to Equipment | DIP1500 Flash Save | BOOL |  |  |  | GVL_MODBUS.DIP1500_Coils[2] | GVL_COM.COM_DIP1500_1.COM_OUTPUT_COILS[2] | TO CHECK | Write channel mode not confirmed (cyclic or trigger)
Coil | 0x0004 | 3 | FC15 Write Multiple Coils | PLC to Equipment | DIP1500 Operation Mode | BOOL |  |  |  | GVL_MODBUS.DIP1500_Coils[3] | GVL_COM.COM_DIP1500_1.COM_OUTPUT_COILS[3] | TO CHECK | Write channel mode not confirmed (cyclic or trigger)
IR | 0x3001 | 0 | FC04 Read Input Registers | Equipment to PLC | DIP1500 Firmware Version | WORD |  | 3+5+8 bits (major+minor+revision) |  | GVL_MODBUS.DIP1500_InputRegisters[0] | GVL_COM.COM_DIP1500_1.COM_INPUT_IR[0] | Read, cyclic
IR | 0x3002 | 1 | FC04 Read Input Registers | Equipment to PLC | DIP1500 Hardware Version | WORD |  | 3+5+8 bits (major+minor+revision) |  | GVL_MODBUS.DIP1500_InputRegisters[1] | GVL_COM.COM_DIP1500_1.COM_INPUT_IR[1] | Read, cyclic
IR | 0x3003 | 2 | FC04 Read Input Registers | Equipment to PLC | DIP1500 Temperature | WORD |  | (raw - 500) / 10 | °C | GVL_MODBUS.DIP1500_InputRegisters[2] | GVL_COM.COM_DIP1500_1.COM_INPUT_IR[2] | Read, cyclic
IR | 0x3004 | 3 | FC04 Read Input Registers | Equipment to PLC | DIP1500 Float Level Alarm | WORD |  | 1 |  | GVL_MODBUS.DIP1500_InputRegisters[3] | GVL_COM.COM_DIP1500_1.COM_INPUT_IR[3] | Read, cyclic
IR | 0x3005 | 4 | FC04 Read Input Registers | Equipment to PLC | DIP1500 Digital Output Value | WORD |  | 1 |  | GVL_MODBUS.DIP1500_InputRegisters[4] | GVL_COM.COM_DIP1500_1.COM_INPUT_IR[4] | Read, cyclic
HR | 0x4001 | 0 | FC16 Write Multiple Registers | PLC to Equipment | DIP1500 Motor Speed | REAL | LSW | 1 | rpm | GVL_MODBUS.DIP1500_Holding_Cmd[0] | GVL_COM.COM_DIP1500_1.COM_OUTPUT_HR_CMD[0] | Write, rising edge of COM_OUTPUT_CMD_TRIGGER
HR | 0x4002 | 1 | FC16 Write Multiple Registers | PLC to Equipment | DIP1500 Motor Speed | REAL | MSW | 1 | rpm | GVL_MODBUS.DIP1500_Holding_Cmd[1] | GVL_COM.COM_DIP1500_1.COM_OUTPUT_HR_CMD[1] | Write, rising edge of COM_OUTPUT_CMD_TRIGGER
HR | 0x4003 | 2 | FC16 Write Multiple Registers | PLC to Equipment | DIP1500 Max Motor Speed | REAL | LSW | 1 | rpm | GVL_MODBUS.DIP1500_Holding_Cmd[2] | GVL_COM.COM_DIP1500_1.COM_OUTPUT_HR_CMD[2] | Write, rising edge of COM_OUTPUT_CMD_TRIGGER
HR | 0x4004 | 3 | FC16 Write Multiple Registers | PLC to Equipment | DIP1500 Max Motor Speed | REAL | MSW | 1 | rpm | GVL_MODBUS.DIP1500_Holding_Cmd[3] | GVL_COM.COM_DIP1500_1.COM_OUTPUT_HR_CMD[3] | Write, rising edge of COM_OUTPUT_CMD_TRIGGER
HR | 0x4005 | 4 | FC16 Write Multiple Registers | PLC to Equipment | DIP1500 Run Time Or Volume | UDINT (time mode) / REAL (volume mode) | LSW | 1 | ms (time mode) / ml (volume mode) | GVL_MODBUS.DIP1500_Holding_Cmd[4] | GVL_COM.COM_DIP1500_1.COM_OUTPUT_HR_CMD[4] | Write, rising edge of COM_OUTPUT_CMD_TRIGGER
HR | 0x4006 | 5 | FC16 Write Multiple Registers | PLC to Equipment | DIP1500 Run Time Or Volume | UDINT (time mode) / REAL (volume mode) | MSW | 1 | ms (time mode) / ml (volume mode) | GVL_MODBUS.DIP1500_Holding_Cmd[5] | GVL_COM.COM_DIP1500_1.COM_OUTPUT_HR_CMD[5] | Write, rising edge of COM_OUTPUT_CMD_TRIGGER
HR | 0x4007 | 0 | FC03 Read Holding Registers | Equipment to PLC | DIP1500 Real-Time Run Time Or Volume | UDINT (time mode) / REAL (volume mode) | LSW | 1 | ms (time mode) / ml (volume mode) | GVL_MODBUS.DIP1500_Holding_Counters[0] | GVL_COM.COM_DIP1500_1.COM_INPUT_HR_COUNTERS[0] | Read, cyclic
HR | 0x4008 | 1 | FC03 Read Holding Registers | Equipment to PLC | DIP1500 Real-Time Run Time Or Volume | UDINT (time mode) / REAL (volume mode) | MSW | 1 | ms (time mode) / ml (volume mode) | GVL_MODBUS.DIP1500_Holding_Counters[1] | GVL_COM.COM_DIP1500_1.COM_INPUT_HR_COUNTERS[1] | Read, cyclic
HR | 0x4009 | 2 | FC03 Read Holding Registers | Equipment to PLC | DIP1500 Accumulated Run Time Or Volume | UDINT (time mode) / REAL (volume mode) | LSW | 1 | ms (time mode) / ml (volume mode) | GVL_MODBUS.DIP1500_Holding_Counters[2] | GVL_COM.COM_DIP1500_1.COM_INPUT_HR_COUNTERS[2] | Read, cyclic
HR | 0x400A | 3 | FC03 Read Holding Registers | Equipment to PLC | DIP1500 Accumulated Run Time Or Volume | UDINT (time mode) / REAL (volume mode) | MSW | 1 | ms (time mode) / ml (volume mode) | GVL_MODBUS.DIP1500_Holding_Counters[3] | GVL_COM.COM_DIP1500_1.COM_INPUT_HR_COUNTERS[3] | Read, cyclic
HR | 0x400B | 0 | FC16 Write Multiple Registers | PLC to Equipment | DIP1500 Flow Rate Or Speed Calibration Coefficient | REAL | LSW | 1 | ml/min or rpm | GVL_MODBUS.DIP1500_Holding_Config[0] | GVL_COM.COM_DIP1500_1.COM_OUTPUT_HR_CONFIG[0] | Write, rising edge of COM_OUTPUT_CONFIG_TRIGGER
HR | 0x400C | 1 | FC16 Write Multiple Registers | PLC to Equipment | DIP1500 Flow Rate Or Speed Calibration Coefficient | REAL | MSW | 1 | ml/min or rpm | GVL_MODBUS.DIP1500_Holding_Config[1] | GVL_COM.COM_DIP1500_1.COM_OUTPUT_HR_CONFIG[1] | Write, rising edge of COM_OUTPUT_CONFIG_TRIGGER
HR | 0x400D | 2 | FC16 Write Multiple Registers | PLC to Equipment | DIP1500 Foot Switch Input Mode | WORD |  | 1 |  | GVL_MODBUS.DIP1500_Holding_Config[2] | GVL_COM.COM_DIP1500_1.COM_OUTPUT_HR_CONFIG[2] | Write, rising edge of COM_OUTPUT_CONFIG_TRIGGER
HR | 0x400E | 3 | FC16 Write Multiple Registers | PLC to Equipment | DIP1500 Liquid Level Input Mode | WORD |  | 1 |  | GVL_MODBUS.DIP1500_Holding_Config[3] | GVL_COM.COM_DIP1500_1.COM_OUTPUT_HR_CONFIG[3] | Write, rising edge of COM_OUTPUT_CONFIG_TRIGGER
HR | 0x400F | 4 | FC16 Write Multiple Registers | PLC to Equipment | DIP1500 State Output Mode | WORD |  | 1 |  | GVL_MODBUS.DIP1500_Holding_Config[4] | GVL_COM.COM_DIP1500_1.COM_OUTPUT_HR_CONFIG[4] | Write, rising edge of COM_OUTPUT_CONFIG_TRIGGER
HR | 0x4010 | 5 | FC16 Write Multiple Registers | PLC to Equipment | DIP1500 Communication Address | WORD |  | 1 |  | GVL_MODBUS.DIP1500_Holding_Config[5] | GVL_COM.COM_DIP1500_1.COM_OUTPUT_HR_CONFIG[5] | Write, rising edge of COM_OUTPUT_CONFIG_TRIGGER
HR | 0x4011 | 6 | FC16 Write Multiple Registers | PLC to Equipment | DIP1500 Baud Rate Index | WORD |  | 1 | index | GVL_MODBUS.DIP1500_Holding_Config[6] | GVL_COM.COM_DIP1500_1.COM_OUTPUT_HR_CONFIG[6] | Write, rising edge of COM_OUTPUT_CONFIG_TRIGGER
Note on A1: Modbus table : Coil, DI (discrete input), IR (input register), HR (holding register).
Note on B1: Register or coil address as written in the equipment manual (hex 0x4001 or decimal).
Note on C1: Position in the CODESYS Modbus channel and in the GVL_MODBUS array (0 = first register of the channel).
Note on D1: Modbus function code used by the CODESYS channel.
Note on E1: Equipment to PLC = read by the PLC. PLC to Equipment = written by the PLC.
Note on F1: Readable name of the value. Used as tag name in FUXA and as label in the supervisions.
Note on G1: Type of the value in the equipment. 32-bit values use 2 rows.
Note on H1: 32-bit value split in 2 registers : MSW = most significant word, LSW = least significant word. Empty for 16-bit and BOOL.
Note on I1: Conversion raw value -> engineering value, as written in the equipment manual. "1" = no conversion.
Note on J1: Engineering unit of the value (free text).
Note on K1: Element of GVL_MODBUS mapped in the CODESYS device I/O mapping (Modbus server or slave channel). GVL_MODBUS = exchange variables only.
Note on L1: Variable of GVL_COM copied to / from GVL_MODBUS by GFC_COM_IN / GFC_COM_OUT.
Note on M1: How the CODESYS Modbus master channel runs : cyclic, or on the rising edge of a trigger variable mapped in the slave I/O mapping.
Note on N1: Free text. Not used by the generator.

## LISTS (hidden)
IEC_DUT | VALUE_TYPE | EXCHANGE | FUNCTION | RTU_DIR | TCP_DIR | WORD | WORD_ORDER | CHANNEL | TABLE | LINE | PLC_PORT | PLC_ROLE | BAUD | PARITY | DATA_BITS | STOP_BITS | TIMEOUT | OBJ_TYPE | INSTANCE | YESNO | COPIED_BY | SLOT | MODULE | MOD_TYPE | IO_TYPE | IOMAP_TYPE | SIGNAL | ZIPLINK | IO_STATUS | RACK_STATUS | CODESYS_DEV | CLIENT | TCP_ROLE | CLIENT_ORDER | KIND | COMM | INTERFACE | READ_CH | SECTION_TCP | FC_EXC | EXC_DIR
BOOL | BOOL | Modbus TCP FUXA Coil | FC01 Read Coils | Equipment to PLC | Client to PLC | MSW | ABCD (MSW first) | Read, cyclic | Coil | RTU_1 | RS-232/485 4-pin | Master | 1200 | None | 7 | 1 | 100 | ADM100W | ADM100W_1 | Yes | GFC_EXC_IN | 1 | P2-16AD-1 | AI | DI | BOOL | 24 VDC | ZL-CBL40-2 / ZL-RTB40-1 | Used | Installed | Module | FUXA | PLC = server | CDAB (Float32MLE) | Equipment | Modbus RTU | RS-485 | Cyclic | COILS | FC_EXC_UPI_LOCAL_FUXA_ADM100W | A -> B
BYTE | WORD | Modbus TCP FUXA DI | FC02 Read Discrete Inputs | PLC to Equipment | PLC to Client | LSW | CDAB (LSW first) | Write, cyclic | DI | RTU_2 | RS-232/485 RJ12 | Slave | 2400 | Even | 8 | 2 | 200 | DOSENSOR | DOSENSOR_1 | No | GFC_EXC_OUT | 2 | P2-16AD-2 | AO | DO | WORD | 4-20 mA | ZL-P2-CBL24-2 / ZL-RTB20-1 | Spare | Empty | Module_1 | HMI | PLC = client | CDAB, confirmed on the PV800 | Functional unit (UPI) | Modbus TCP | RS-232 | Rising edge | DISCRETE_INPUTS | FC_EXC_UPI_LOCAL_HMI_ADM100W | B -> A
WORD | INT | Modbus TCP FUXA IR | FC03 Read Holding Registers |  |  |  | BADC (byte swap) | Read, rising edge | IR | RTU_3 | TO CHECK |  | 4800 | Odd | TO CHECK | TO CHECK | 500 | DIP1500 | DIP1500_1 |  |  | 3 | P2-16DA-1 | DI | AI | DWORD | 0-20 mA |  | Reserved | Planned | Module_2 | WEBVISU |  | ABCD (Float32) |  | EtherNet/IP |  | Application | INPUT_REGISTERS | FC_EXC_UPI_LOCAL_WEBVISU_ADM100W
DWORD | UINT | Modbus TCP FUXA HR | FC04 Read Input Registers |  |  |  | DCBA (byte and word swap) | Write, rising edge of COM_OUTPUT_CMD_TRIGGER | HR |  |  |  | 9600 | TO CHECK |  |  | 1000 | UPI_LOCAL_FUXA | UPI_LOCAL_FUXA |  |  | 4 | P2-16DA-2 | DO | AO | INT | 0-10 V |  | TO CHECK | TO CHECK | Module_3 |  |  | TO CHECK |  | Wired I/O |  |  | HOLDING_REGISTERS | FC_EXC_UPI_LOCAL_FUXA_DOSENSOR
LWORD | DINT | Modbus TCP HMI Coil | FC05 Write Single Coil |  |  |  |  | Write, rising edge of COM_OUTPUT_CONFIG_TRIGGER |  |  |  |  | 19200 |  |  |  | 2000 | UPI_LOCAL_HMI | UPI_LOCAL_HMI |  |  | 5 | P2-08AD-1 | EMPTY |  | DINT | +/-10 V |  |  |  | Module_4 |  |  |  |  | None |  |  |  | FC_EXC_UPI_LOCAL_HMI_DOSENSOR
SINT | UDINT | Modbus TCP HMI DI | FC06 Write Single Register |  |  |  |  | Read, application |  |  |  |  | 38400 |  |  |  | TO CHECK | UPI_LOCAL_WEBVISU | UPI_LOCAL_WEBVISU |  |  | 6 | P2-08DA-1 |  |  | UINT | Dry contact |  |  |  | Module_5 | [8 empty] | FC_EXC_UPI_LOCAL_WEBVISU_DOSENSOR
INT | REAL | Modbus TCP HMI IR | FC15 Write Multiple Coils |  |  |  |  | Write, application |  |  |  |  | 57600 | [5 empty] | <INSTANCE> |  |  | 7 | P2-32ND3-1 |  |  | UDINT |  |  |  |  | Module_6 | [8 empty] | FC_EXC_UPI_LOCAL_FUXA_DIP1500
DINT | UDINT (time mode) / REAL (volume mode) | Modbus TCP HMI HR | FC16 Write Multiple Registers |  |  |  |  | TO CHECK |  |  |  |  | 115200 | [5 empty] | <INSTANCE_B> |  |  | 8 | P2-16ND3 |  |  | REAL |  |  |  |  | Module_7 | [8 empty] | FC_EXC_UPI_LOCAL_HMI_DIP1500
LINT |  | WebVisu (direct variable access) | FC23 Read/Write Multiple Registers | [9 empty] | TO CHECK | [8 empty] | 9 | P2-32NE3 | [7 empty] | Module_8 | [8 empty] | FC_EXC_UPI_LOCAL_WEBVISU_DIP1500
USINT |  | Modbus RTU (see RTU tables) | [19 empty] | 10 | P2-32TD1P | [7 empty] | Module_9
UINT |  | Modbus RTU write trigger (slave I/O mapping) | [19 empty] | 11 | P2-32TD2P | [7 empty] | Module_10
UDINT |  | Physical I/O (GVL_IOMAP, GFC_IO) | [20 empty] | P2-16TD2P
ULINT |  | Exchange (GFC_EXC) | [20 empty] | P2-08TRS
REAL |  | Persistent parameter (GVL_PA) | [20 empty] | P2-FILL
LREAL
TIME
STRING
DUT_Union_Real_Word
TON
TOF
TP
R_TRIG
F_TRIG
ARRAY[0..1] OF WORD
ARRAY[0..7] OF BOOL