## README
Modbus TCP exchanges
All Modbus TCP exchanges where the PLC is the server (supervisions, HMI, other devices later).
Sheets:
CLIENTS : one row per client, with its reserved address range
COILS, DISCRETE_INPUTS, INPUT_REGISTERS, HOLDING_REGISTERS : one row per address used
Rules:
Modbus address : coils and registers from 1, discrete inputs from 10001
Client address : address typed in the client (FUXA uses 100001.. for discrete inputs)
A 32-bit REAL uses 2 rows (Word = LSW then MSW, low word first)
Direction : Client to PLC (coils, holding registers) or PLC to Client (discrete inputs, input registers)
A new client takes a new address range : add it in CLIENTS first
Cells marked "TO CHECK" (yellow) are values not confirmed yet.

## CLIENTS
Client | Description | Role | Address range | Word order (32-bit) | IP address | Comment
FUXA | SCADA (FUXA on the Raspberry Pi) | PLC = server | Coils 1-1000, DI 10001-11000, IR 1-1000, HR 1-1000 | CDAB (Float32MLE) | TO CHECK
HMI | Local HMI panel (Rockwell PanelView 800) | PLC = server | FUXA address + 1000 | CDAB, confirmed on the PV800 | TO CHECK | Enter Key Handshake disabled for numeric entries
Note on A1: Supervision or device that reads / writes the address. Each client has its own address range (sheet CLIENTS).
Note on B1: Readable description.
Note on C1: Role of the PLC for this client.
Note on D1: Addresses reserved for the client in each table.
Note on E1: Word order of 32-bit values for this client.
Note on F1: IP address of the client.
Note on G1: Free text. In TEMPLATE_TCP : sheet of MODBUS_TCP where the row goes.

## COILS
Modbus address | Client address | Client | Instance | Name | Direction | Type | Word | Scale | Unit | GVL_MODBUS variable | GVL_COM variable | Comment
1 | 1 | FUXA | DOSENSOR_1 | DO Calibration High | Client to PLC | BOOL |  |  |  | GVL_MODBUS.Coils_TCP_HMI[0].0 | GVL_COM.COM_DOSENSOR_1.SCADA_INPUT_CALIBRATION_HIGH
2 | 2 | FUXA | DOSENSOR_1 | DO Calibration Low | Client to PLC | BOOL |  |  |  | GVL_MODBUS.Coils_TCP_HMI[0].1 | GVL_COM.COM_DOSENSOR_1.SCADA_INPUT_CALIBRATION_LOW
3 | 3 | FUXA | DIP1500_1 | DIP1500 Motor Start Stop | Client to PLC | BOOL |  |  |  | GVL_MODBUS.Coils_TCP_HMI[0].2 | GVL_COM.COM_DIP1500_1.SCADA_INPUT_MOTOR_START_STOP
4 | 4 | FUXA | DIP1500_1 | DIP1500 Motor Direction | Client to PLC | BOOL |  |  |  | GVL_MODBUS.Coils_TCP_HMI[0].3 | GVL_COM.COM_DIP1500_1.SCADA_INPUT_MOTOR_DIRECTION
5 | 5 | FUXA | DIP1500_1 | DIP1500 Flash Save | Client to PLC | BOOL |  |  |  | GVL_MODBUS.Coils_TCP_HMI[0].4 | GVL_COM.COM_DIP1500_1.SCADA_INPUT_FLASH_SAVE
6 | 6 | FUXA | DIP1500_1 | DIP1500 Operation Mode | Client to PLC | BOOL |  |  |  | GVL_MODBUS.Coils_TCP_HMI[0].5 | GVL_COM.COM_DIP1500_1.SCADA_INPUT_OPERATION_MODE
7 | 7 | FUXA | DIP1500_1 | DIP1500 Parameter Write Enable | Client to PLC | BOOL |  |  |  | GVL_MODBUS.Coils_TCP_HMI[0].6 | GVL_COM.COM_DIP1500_1.SCADA_INPUT_PARAM_WRITE_ENABLE
8 | 8 | FUXA | DOSENSOR_1 | DO Sensor Local Request | Client to PLC | BOOL |  |  |  | GVL_MODBUS.Coils_TCP_HMI[0].7 | GVL_COM.COM_DOSENSOR_1.SCADA_INPUT_LOCAL_REQUEST
9 | 9 | FUXA | DOSENSOR_1 | DO Sensor Auto Request | Client to PLC | BOOL |  |  |  | GVL_MODBUS.Coils_TCP_HMI[1].0 | GVL_COM.COM_DOSENSOR_1.SCADA_INPUT_AUTO_REQUEST
10 | 10 | FUXA | DIP1500_1 | DIP1500 Local Request | Client to PLC | BOOL |  |  |  | GVL_MODBUS.Coils_TCP_HMI[1].1 | GVL_COM.COM_DIP1500_1.SCADA_INPUT_LOCAL_REQUEST
11 | 11 | FUXA | DIP1500_1 | DIP1500 Auto Request | Client to PLC | BOOL |  |  |  | GVL_MODBUS.Coils_TCP_HMI[1].2 | GVL_COM.COM_DIP1500_1.SCADA_INPUT_AUTO_REQUEST
12 | 12 | FUXA | ADM100W_1 | ADM100W Local Request | Client to PLC | BOOL |  |  |  | GVL_MODBUS.Coils_TCP_HMI[1].3 | GVL_COM.COM_ADM100W_1.SCADA_INPUT_LOCAL_REQUEST
13 | 13 | FUXA | ADM100W_1 | ADM100W Auto Request | Client to PLC | BOOL |  |  |  | GVL_MODBUS.Coils_TCP_HMI[1].4 | GVL_COM.COM_ADM100W_1.SCADA_INPUT_AUTO_REQUEST
14 | 14 | FUXA | UPI_LOCAL_FUXA | Global Local FUXA Request | Client to PLC | BOOL |  |  |  | GVL_MODBUS.Coils_TCP_HMI[1].5 | GVL_COM.COM_UPI_LOCAL_FUXA.SCADA_INPUT_LOCAL_REQUEST
15 | 15 | FUXA | UPI_LOCAL_FUXA | Global Auto FUXA Request | Client to PLC | BOOL |  |  |  | GVL_MODBUS.Coils_TCP_HMI[1].6 | GVL_COM.COM_UPI_LOCAL_FUXA.SCADA_INPUT_AUTO_REQUEST
1001 | 1001 | HMI | DOSENSOR_1 | DO Calibration High | Client to PLC | BOOL |  |  |  | GVL_MODBUS.Coils_TCP_HMI[125].0 | GVL_COM.COM_DOSENSOR_1.HMI_INPUT_CALIBRATION_HIGH
1002 | 1002 | HMI | DOSENSOR_1 | DO Calibration Low | Client to PLC | BOOL |  |  |  | GVL_MODBUS.Coils_TCP_HMI[125].1 | GVL_COM.COM_DOSENSOR_1.HMI_INPUT_CALIBRATION_LOW
1003 | 1003 | HMI | DIP1500_1 | DIP1500 Motor Start Stop | Client to PLC | BOOL |  |  |  | GVL_MODBUS.Coils_TCP_HMI[125].2 | GVL_COM.COM_DIP1500_1.HMI_INPUT_MOTOR_START_STOP
1004 | 1004 | HMI | DIP1500_1 | DIP1500 Motor Direction | Client to PLC | BOOL |  |  |  | GVL_MODBUS.Coils_TCP_HMI[125].3 | GVL_COM.COM_DIP1500_1.HMI_INPUT_MOTOR_DIRECTION
1005 | 1005 | HMI | DIP1500_1 | DIP1500 Flash Save | Client to PLC | BOOL |  |  |  | GVL_MODBUS.Coils_TCP_HMI[125].4 | GVL_COM.COM_DIP1500_1.HMI_INPUT_FLASH_SAVE
1006 | 1006 | HMI | DIP1500_1 | DIP1500 Operation Mode | Client to PLC | BOOL |  |  |  | GVL_MODBUS.Coils_TCP_HMI[125].5 | GVL_COM.COM_DIP1500_1.HMI_INPUT_OPERATION_MODE
1007 | 1007 | HMI | DIP1500_1 | DIP1500 Parameter Write Enable | Client to PLC | BOOL |  |  |  | GVL_MODBUS.Coils_TCP_HMI[125].6 | GVL_COM.COM_DIP1500_1.HMI_INPUT_PARAM_WRITE_ENABLE
1008 | 1008 | HMI | DOSENSOR_1 | DO Sensor Local Request | Client to PLC | BOOL |  |  |  | GVL_MODBUS.Coils_TCP_HMI[125].7 | GVL_COM.COM_DOSENSOR_1.HMI_INPUT_LOCAL_REQUEST
1009 | 1009 | HMI | DOSENSOR_1 | DO Sensor Auto Request | Client to PLC | BOOL |  |  |  | GVL_MODBUS.Coils_TCP_HMI[126].0 | GVL_COM.COM_DOSENSOR_1.HMI_INPUT_AUTO_REQUEST
1010 | 1010 | HMI | DIP1500_1 | DIP1500 Local Request | Client to PLC | BOOL |  |  |  | GVL_MODBUS.Coils_TCP_HMI[126].1 | GVL_COM.COM_DIP1500_1.HMI_INPUT_LOCAL_REQUEST
1011 | 1011 | HMI | DIP1500_1 | DIP1500 Auto Request | Client to PLC | BOOL |  |  |  | GVL_MODBUS.Coils_TCP_HMI[126].2 | GVL_COM.COM_DIP1500_1.HMI_INPUT_AUTO_REQUEST
1012 | 1012 | HMI | ADM100W_1 | ADM100W Local Request | Client to PLC | BOOL |  |  |  | GVL_MODBUS.Coils_TCP_HMI[126].3 | GVL_COM.COM_ADM100W_1.HMI_INPUT_LOCAL_REQUEST
1013 | 1013 | HMI | ADM100W_1 | ADM100W Auto Request | Client to PLC | BOOL |  |  |  | GVL_MODBUS.Coils_TCP_HMI[126].4 | GVL_COM.COM_ADM100W_1.HMI_INPUT_AUTO_REQUEST
1014 | 1014 | HMI | UPI_LOCAL_HMI | Global Local HMI Request | Client to PLC | BOOL |  |  |  | GVL_MODBUS.Coils_TCP_HMI[126].5 | GVL_COM.COM_UPI_LOCAL_HMI.HMI_INPUT_LOCAL_REQUEST
1015 | 1015 | HMI | UPI_LOCAL_HMI | Global Auto HMI Request | Client to PLC | BOOL |  |  |  | GVL_MODBUS.Coils_TCP_HMI[126].6 | GVL_COM.COM_UPI_LOCAL_HMI.HMI_INPUT_AUTO_REQUEST
Note on A1: Address in the PLC Modbus TCP server : coils and registers from 1, discrete inputs from 10001. GVL_MODBUS index = address - 1 (discrete inputs : address - 10001).
Note on B1: Address typed in the client. FUXA : discrete inputs 100001.., others = Modbus address.
Note on C1: Supervision or device that reads / writes the address. Each client has its own address range (sheet CLIENTS).
Note on D1: Instance that owns the value (GVL_COM.COM_<instance>).
Note on E1: Readable name of the value. Used as tag name in FUXA and as label in the supervisions.
Note on F1: Client to PLC : coils and holding registers written by the client. PLC to Client : discrete inputs and input registers read by the client.
Note on G1: Type of the value seen by the client. REAL uses 2 registers.
Note on H1: 32-bit value split in 2 registers : MSW = most significant word, LSW = least significant word. Empty for 16-bit and BOOL.
Note on I1: Conversion raw value -> engineering value, as written in the equipment manual. "1" = no conversion.
Note on J1: Engineering unit of the value (free text).
Note on K1: Element of GVL_MODBUS mapped in the CODESYS device I/O mapping (Modbus server or slave channel). GVL_MODBUS = exchange variables only.
Note on L1: Variable of GVL_COM copied to / from GVL_MODBUS by GFC_COM_IN / GFC_COM_OUT.
Note on M1: Free text. In TEMPLATE_TCP : sheet of MODBUS_TCP where the row goes.

## DISCRETE_INPUTS
Modbus address | Client address | Client | Instance | Name | Direction | Type | Word | Scale | Unit | GVL_MODBUS variable | GVL_COM variable | Comment
10001 | 100001 | FUXA | DOSENSOR_1 | Do sensor fault | PLC to Client | BOOL |  |  |  | GVL_MODBUS.Discret_input_TCP_HMI[0].0 | GVL_COM.COM_DOSENSOR_1.SCADA_OUTPUT_FAULT
10002 | 100002 | FUXA | DOSENSOR_1 | Do sensor calibration done | PLC to Client | BOOL |  |  |  | GVL_MODBUS.Discret_input_TCP_HMI[0].1 | GVL_COM.COM_DOSENSOR_1.SCADA_OUTPUT_CALIBRATION_DONE
10003 | 100003 | FUXA | ADM100W_1 | ADM100W Alarm 1 Status | PLC to Client | BOOL |  |  |  | GVL_MODBUS.Discret_input_TCP_HMI[0].2 | GVL_COM.COM_ADM100W_1.SCADA_OUTPUT_ALARM_1_STATUS
10004 | 100004 | FUXA | ADM100W_1 | ADM100W Alarm 2 Status | PLC to Client | BOOL |  |  |  | GVL_MODBUS.Discret_input_TCP_HMI[0].3 | GVL_COM.COM_ADM100W_1.SCADA_OUTPUT_ALARM_2_STATUS
10005 | 100005 | FUXA | ADM100W_1 | ADM100W Alarm 3 Status | PLC to Client | BOOL |  |  |  | GVL_MODBUS.Discret_input_TCP_HMI[0].4 | GVL_COM.COM_ADM100W_1.SCADA_OUTPUT_ALARM_3_STATUS
10006 | 100006 | FUXA | ADM100W_1 | ADM100W Alarm 4 Status | PLC to Client | BOOL |  |  |  | GVL_MODBUS.Discret_input_TCP_HMI[0].5 | GVL_COM.COM_ADM100W_1.SCADA_OUTPUT_ALARM_4_STATUS
10007 | 100007 | FUXA | ADM100W_1 | ADM100W Alarm 5 Status | PLC to Client | BOOL |  |  |  | GVL_MODBUS.Discret_input_TCP_HMI[0].6 | GVL_COM.COM_ADM100W_1.SCADA_OUTPUT_ALARM_5_STATUS
10008 | 100008 | FUXA | ADM100W_1 | ADM100W Alarm 6 Status | PLC to Client | BOOL |  |  |  | GVL_MODBUS.Discret_input_TCP_HMI[0].7 | GVL_COM.COM_ADM100W_1.SCADA_OUTPUT_ALARM_6_STATUS
10009 | 100009 | FUXA | ADM100W_1 | ADM100W Alarm 7 Status | PLC to Client | BOOL |  |  |  | GVL_MODBUS.Discret_input_TCP_HMI[1].0 | GVL_COM.COM_ADM100W_1.SCADA_OUTPUT_ALARM_7_STATUS
10010 | 100010 | FUXA | ADM100W_1 | ADM100W Alarm 8 Status | PLC to Client | BOOL |  |  |  | GVL_MODBUS.Discret_input_TCP_HMI[1].1 | GVL_COM.COM_ADM100W_1.SCADA_OUTPUT_ALARM_8_STATUS
10011 | 100011 | FUXA | ADM100W_1 | ADM100W Alarm 9 Status | PLC to Client | BOOL |  |  |  | GVL_MODBUS.Discret_input_TCP_HMI[1].2 | GVL_COM.COM_ADM100W_1.SCADA_OUTPUT_ALARM_9_STATUS
10012 | 100012 | FUXA | ADM100W_1 | ADM100W Alarm 10 Status | PLC to Client | BOOL |  |  |  | GVL_MODBUS.Discret_input_TCP_HMI[1].3 | GVL_COM.COM_ADM100W_1.SCADA_OUTPUT_ALARM_10_STATUS
10013 | 100013 | FUXA | DOSENSOR_1 | DO Sensor Local FUXA Active | PLC to Client | BOOL |  |  |  | GVL_MODBUS.Discret_input_TCP_HMI[1].4 | GVL_COM.COM_DOSENSOR_1.SCADA_OUTPUT_LOCAL_FUXA_ACTIVE
10014 | 100014 | FUXA | DOSENSOR_1 | DO Sensor Local HMI Active | PLC to Client | BOOL |  |  |  | GVL_MODBUS.Discret_input_TCP_HMI[1].5 | GVL_COM.COM_DOSENSOR_1.SCADA_OUTPUT_LOCAL_HMI_ACTIVE
10015 | 100015 | FUXA | DIP1500_1 | DIP1500 Local FUXA Active | PLC to Client | BOOL |  |  |  | GVL_MODBUS.Discret_input_TCP_HMI[1].6 | GVL_COM.COM_DIP1500_1.SCADA_OUTPUT_LOCAL_FUXA_ACTIVE
10016 | 100016 | FUXA | DIP1500_1 | DIP1500 Local HMI Active | PLC to Client | BOOL |  |  |  | GVL_MODBUS.Discret_input_TCP_HMI[1].7 | GVL_COM.COM_DIP1500_1.SCADA_OUTPUT_LOCAL_HMI_ACTIVE
10017 | 100017 | FUXA | ADM100W_1 | ADM100W Local FUXA Active | PLC to Client | BOOL |  |  |  | GVL_MODBUS.Discret_input_TCP_HMI[2].0 | GVL_COM.COM_ADM100W_1.SCADA_OUTPUT_LOCAL_FUXA_ACTIVE
10018 | 100018 | FUXA | ADM100W_1 | ADM100W Local HMI Active | PLC to Client | BOOL |  |  |  | GVL_MODBUS.Discret_input_TCP_HMI[2].1 | GVL_COM.COM_ADM100W_1.SCADA_OUTPUT_LOCAL_HMI_ACTIVE
10019 | 100019 | FUXA | UPI_LOCAL_FUXA | Global Local FUXA Active | PLC to Client | BOOL |  |  |  | GVL_MODBUS.Discret_input_TCP_HMI[2].2 | GVL_COM.COM_UPI_LOCAL_FUXA.SCADA_OUTPUT_LOCAL_ACTIVE
10020 | 100020 | FUXA | UPI_LOCAL_HMI | Global Local HMI Active | PLC to Client | BOOL |  |  |  | GVL_MODBUS.Discret_input_TCP_HMI[2].3 | GVL_COM.COM_UPI_LOCAL_HMI.SCADA_OUTPUT_LOCAL_ACTIVE
11001 | 11001 | HMI | DOSENSOR_1 | Do sensor fault | PLC to Client | BOOL |  |  |  | GVL_MODBUS.Discret_input_TCP_HMI[125].0 | GVL_COM.COM_DOSENSOR_1.HMI_OUTPUT_FAULT
11002 | 11002 | HMI | DOSENSOR_1 | Do sensor calibration done | PLC to Client | BOOL |  |  |  | GVL_MODBUS.Discret_input_TCP_HMI[125].1 | GVL_COM.COM_DOSENSOR_1.HMI_OUTPUT_CALIBRATION_DONE
11003 | 11003 | HMI | ADM100W_1 | ADM100W Alarm 1 Status | PLC to Client | BOOL |  |  |  | GVL_MODBUS.Discret_input_TCP_HMI[125].2 | GVL_COM.COM_ADM100W_1.HMI_OUTPUT_ALARM_1_STATUS
11004 | 11004 | HMI | ADM100W_1 | ADM100W Alarm 2 Status | PLC to Client | BOOL |  |  |  | GVL_MODBUS.Discret_input_TCP_HMI[125].3 | GVL_COM.COM_ADM100W_1.HMI_OUTPUT_ALARM_2_STATUS
11005 | 11005 | HMI | ADM100W_1 | ADM100W Alarm 3 Status | PLC to Client | BOOL |  |  |  | GVL_MODBUS.Discret_input_TCP_HMI[125].4 | GVL_COM.COM_ADM100W_1.HMI_OUTPUT_ALARM_3_STATUS
11006 | 11006 | HMI | ADM100W_1 | ADM100W Alarm 4 Status | PLC to Client | BOOL |  |  |  | GVL_MODBUS.Discret_input_TCP_HMI[125].5 | GVL_COM.COM_ADM100W_1.HMI_OUTPUT_ALARM_4_STATUS
11007 | 11007 | HMI | ADM100W_1 | ADM100W Alarm 5 Status | PLC to Client | BOOL |  |  |  | GVL_MODBUS.Discret_input_TCP_HMI[125].6 | GVL_COM.COM_ADM100W_1.HMI_OUTPUT_ALARM_5_STATUS
11008 | 11008 | HMI | ADM100W_1 | ADM100W Alarm 6 Status | PLC to Client | BOOL |  |  |  | GVL_MODBUS.Discret_input_TCP_HMI[125].7 | GVL_COM.COM_ADM100W_1.HMI_OUTPUT_ALARM_6_STATUS
11009 | 11009 | HMI | ADM100W_1 | ADM100W Alarm 7 Status | PLC to Client | BOOL |  |  |  | GVL_MODBUS.Discret_input_TCP_HMI[126].0 | GVL_COM.COM_ADM100W_1.HMI_OUTPUT_ALARM_7_STATUS
11010 | 11010 | HMI | ADM100W_1 | ADM100W Alarm 8 Status | PLC to Client | BOOL |  |  |  | GVL_MODBUS.Discret_input_TCP_HMI[126].1 | GVL_COM.COM_ADM100W_1.HMI_OUTPUT_ALARM_8_STATUS
11011 | 11011 | HMI | ADM100W_1 | ADM100W Alarm 9 Status | PLC to Client | BOOL |  |  |  | GVL_MODBUS.Discret_input_TCP_HMI[126].2 | GVL_COM.COM_ADM100W_1.HMI_OUTPUT_ALARM_9_STATUS
11012 | 11012 | HMI | ADM100W_1 | ADM100W Alarm 10 Status | PLC to Client | BOOL |  |  |  | GVL_MODBUS.Discret_input_TCP_HMI[126].3 | GVL_COM.COM_ADM100W_1.HMI_OUTPUT_ALARM_10_STATUS
11014 | 11014 | HMI | DOSENSOR_1 | DO Sensor Local Active | PLC to Client | BOOL |  |  |  | GVL_MODBUS.Discret_input_TCP_HMI[126].5 | GVL_COM.COM_DOSENSOR_1.HMI_OUTPUT_LOCAL_ACTIVE
11016 | 11016 | HMI | DIP1500_1 | DIP1500 Local Active | PLC to Client | BOOL |  |  |  | GVL_MODBUS.Discret_input_TCP_HMI[126].7 | GVL_COM.COM_DIP1500_1.HMI_OUTPUT_LOCAL_ACTIVE
11018 | 11018 | HMI | ADM100W_1 | ADM100W Local Active | PLC to Client | BOOL |  |  |  | GVL_MODBUS.Discret_input_TCP_HMI[127].1 | GVL_COM.COM_ADM100W_1.HMI_OUTPUT_LOCAL_ACTIVE
11020 | 11020 | HMI | UPI_LOCAL_HMI | Global Local HMI Active | PLC to Client | BOOL |  |  |  | GVL_MODBUS.Discret_input_TCP_HMI[127].3 | GVL_COM.COM_UPI_LOCAL_HMI.HMI_OUTPUT_LOCAL_ACTIVE
Note on A1: Address in the PLC Modbus TCP server : coils and registers from 1, discrete inputs from 10001. GVL_MODBUS index = address - 1 (discrete inputs : address - 10001).
Note on B1: Address typed in the client. FUXA : discrete inputs 100001.., others = Modbus address.
Note on C1: Supervision or device that reads / writes the address. Each client has its own address range (sheet CLIENTS).
Note on D1: Instance that owns the value (GVL_COM.COM_<instance>).
Note on E1: Readable name of the value. Used as tag name in FUXA and as label in the supervisions.
Note on F1: Client to PLC : coils and holding registers written by the client. PLC to Client : discrete inputs and input registers read by the client.
Note on G1: Type of the value seen by the client. REAL uses 2 registers.
Note on H1: 32-bit value split in 2 registers : MSW = most significant word, LSW = least significant word. Empty for 16-bit and BOOL.
Note on I1: Conversion raw value -> engineering value, as written in the equipment manual. "1" = no conversion.
Note on J1: Engineering unit of the value (free text).
Note on K1: Element of GVL_MODBUS mapped in the CODESYS device I/O mapping (Modbus server or slave channel). GVL_MODBUS = exchange variables only.
Note on L1: Variable of GVL_COM copied to / from GVL_MODBUS by GFC_COM_IN / GFC_COM_OUT.
Note on M1: Free text. In TEMPLATE_TCP : sheet of MODBUS_TCP where the row goes.

## INPUT_REGISTERS
Modbus address | Client address | Client | Instance | Name | Direction | Type | Word | Scale | Unit | GVL_MODBUS variable | GVL_COM variable | Comment
1 | 1 | FUXA | ADM100W_1 | ADM100W Frequency | PLC to Client | REAL | LSW | 1 | Hz | GVL_MODBUS.Input_register_TCP_HMI[0] | GVL_COM.COM_ADM100W_1.SCADA_OUTPUT_FREQUENCY.Word_value[0]
2 | 2 | FUXA | ADM100W_1 | ADM100W Frequency | PLC to Client | REAL | MSW | 1 | Hz | GVL_MODBUS.Input_register_TCP_HMI[1] | GVL_COM.COM_ADM100W_1.SCADA_OUTPUT_FREQUENCY.Word_value[1]
3 | 3 | FUXA | ADM100W_1 | ADM100W L1-L2 Voltage | PLC to Client | REAL | LSW | 1 | V | GVL_MODBUS.Input_register_TCP_HMI[2] | GVL_COM.COM_ADM100W_1.SCADA_OUTPUT_L1_L2_VOLTAGE.Word_value[0]
4 | 4 | FUXA | ADM100W_1 | ADM100W L1-L2 Voltage | PLC to Client | REAL | MSW | 1 | V | GVL_MODBUS.Input_register_TCP_HMI[3] | GVL_COM.COM_ADM100W_1.SCADA_OUTPUT_L1_L2_VOLTAGE.Word_value[1]
5 | 5 | FUXA | ADM100W_1 | ADM100W L1-N Voltage | PLC to Client | REAL | LSW | 1 | V | GVL_MODBUS.Input_register_TCP_HMI[4] | GVL_COM.COM_ADM100W_1.SCADA_OUTPUT_L1_N_VOLTAGE.Word_value[0]
6 | 6 | FUXA | ADM100W_1 | ADM100W L1-N Voltage | PLC to Client | REAL | MSW | 1 | V | GVL_MODBUS.Input_register_TCP_HMI[5] | GVL_COM.COM_ADM100W_1.SCADA_OUTPUT_L1_N_VOLTAGE.Word_value[1]
7 | 7 | FUXA | ADM100W_1 | ADM100W L1 Current | PLC to Client | REAL | LSW | 1 | A | GVL_MODBUS.Input_register_TCP_HMI[6] | GVL_COM.COM_ADM100W_1.SCADA_OUTPUT_L1_CURRENT.Word_value[0]
8 | 8 | FUXA | ADM100W_1 | ADM100W L1 Current | PLC to Client | REAL | MSW | 1 | A | GVL_MODBUS.Input_register_TCP_HMI[7] | GVL_COM.COM_ADM100W_1.SCADA_OUTPUT_L1_CURRENT.Word_value[1]
9 | 9 | FUXA | ADM100W_1 | ADM100W L1 Active Power | PLC to Client | REAL | LSW | 1 | per ADM100W config | GVL_MODBUS.Input_register_TCP_HMI[8] | GVL_COM.COM_ADM100W_1.SCADA_OUTPUT_L1_ACTIVE_POWER.Word_value[0]
10 | 10 | FUXA | ADM100W_1 | ADM100W L1 Active Power | PLC to Client | REAL | MSW | 1 | per ADM100W config | GVL_MODBUS.Input_register_TCP_HMI[9] | GVL_COM.COM_ADM100W_1.SCADA_OUTPUT_L1_ACTIVE_POWER.Word_value[1]
11 | 11 | FUXA | ADM100W_1 | ADM100W L1 Apparent Power | PLC to Client | REAL | LSW | 1 | per ADM100W config | GVL_MODBUS.Input_register_TCP_HMI[10] | GVL_COM.COM_ADM100W_1.SCADA_OUTPUT_L1_APPARENT_POWER.Word_value[0]
12 | 12 | FUXA | ADM100W_1 | ADM100W L1 Apparent Power | PLC to Client | REAL | MSW | 1 | per ADM100W config | GVL_MODBUS.Input_register_TCP_HMI[11] | GVL_COM.COM_ADM100W_1.SCADA_OUTPUT_L1_APPARENT_POWER.Word_value[1]
13 | 13 | FUXA | ADM100W_1 | ADM100W L1 Reactive Power | PLC to Client | REAL | LSW | 1 | per ADM100W config | GVL_MODBUS.Input_register_TCP_HMI[12] | GVL_COM.COM_ADM100W_1.SCADA_OUTPUT_L1_REACTIVE_POWER.Word_value[0]
14 | 14 | FUXA | ADM100W_1 | ADM100W L1 Reactive Power | PLC to Client | REAL | MSW | 1 | per ADM100W config | GVL_MODBUS.Input_register_TCP_HMI[13] | GVL_COM.COM_ADM100W_1.SCADA_OUTPUT_L1_REACTIVE_POWER.Word_value[1]
15 | 15 | FUXA | ADM100W_1 | ADM100W L1 Current Phase Angle | PLC to Client | REAL | LSW | 1 | ° | GVL_MODBUS.Input_register_TCP_HMI[14] | GVL_COM.COM_ADM100W_1.SCADA_OUTPUT_L1_CURRENT_PHASE_ANGLE.Word_value[0]
16 | 16 | FUXA | ADM100W_1 | ADM100W L1 Current Phase Angle | PLC to Client | REAL | MSW | 1 | ° | GVL_MODBUS.Input_register_TCP_HMI[15] | GVL_COM.COM_ADM100W_1.SCADA_OUTPUT_L1_CURRENT_PHASE_ANGLE.Word_value[1]
17 | 17 | FUXA | ADM100W_1 | ADM100W L1 Power Factor | PLC to Client | REAL | LSW | 1 |  | GVL_MODBUS.Input_register_TCP_HMI[16] | GVL_COM.COM_ADM100W_1.SCADA_OUTPUT_L1_POWER_FACTOR.Word_value[0]
18 | 18 | FUXA | ADM100W_1 | ADM100W L1 Power Factor | PLC to Client | REAL | MSW | 1 |  | GVL_MODBUS.Input_register_TCP_HMI[17] | GVL_COM.COM_ADM100W_1.SCADA_OUTPUT_L1_POWER_FACTOR.Word_value[1]
19 | 19 | FUXA | ADM100W_1 | ADM100W L1 Voltage THD | PLC to Client | REAL | LSW | 1 | % | GVL_MODBUS.Input_register_TCP_HMI[18] | GVL_COM.COM_ADM100W_1.SCADA_OUTPUT_L1_VOLTAGE_THD.Word_value[0]
20 | 20 | FUXA | ADM100W_1 | ADM100W L1 Voltage THD | PLC to Client | REAL | MSW | 1 | % | GVL_MODBUS.Input_register_TCP_HMI[19] | GVL_COM.COM_ADM100W_1.SCADA_OUTPUT_L1_VOLTAGE_THD.Word_value[1]
21 | 21 | FUXA | ADM100W_1 | ADM100W L1 Current THD | PLC to Client | REAL | LSW | 1 | % | GVL_MODBUS.Input_register_TCP_HMI[20] | GVL_COM.COM_ADM100W_1.SCADA_OUTPUT_L1_CURRENT_THD.Word_value[0]
22 | 22 | FUXA | ADM100W_1 | ADM100W L1 Current THD | PLC to Client | REAL | MSW | 1 | % | GVL_MODBUS.Input_register_TCP_HMI[21] | GVL_COM.COM_ADM100W_1.SCADA_OUTPUT_L1_CURRENT_THD.Word_value[1]
23 | 23 | FUXA | ADM100W_1 | ADM100W L1 Max Load | PLC to Client | REAL | LSW | 1 | per ADM100W config | GVL_MODBUS.Input_register_TCP_HMI[22] | GVL_COM.COM_ADM100W_1.SCADA_OUTPUT_L1_MAX_LOAD.Word_value[0]
24 | 24 | FUXA | ADM100W_1 | ADM100W L1 Max Load | PLC to Client | REAL | MSW | 1 | per ADM100W config | GVL_MODBUS.Input_register_TCP_HMI[23] | GVL_COM.COM_ADM100W_1.SCADA_OUTPUT_L1_MAX_LOAD.Word_value[1]
25 | 25 | FUXA | ADM100W_1 | ADM100W L1-L2 Voltage Phase Angle | PLC to Client | REAL | LSW | 1 | ° | GVL_MODBUS.Input_register_TCP_HMI[24] | GVL_COM.COM_ADM100W_1.SCADA_OUTPUT_L1_L2_VOLTAGE_PHASE_ANGLE.Word_value[0]
26 | 26 | FUXA | ADM100W_1 | ADM100W L1-L2 Voltage Phase Angle | PLC to Client | REAL | MSW | 1 | ° | GVL_MODBUS.Input_register_TCP_HMI[25] | GVL_COM.COM_ADM100W_1.SCADA_OUTPUT_L1_L2_VOLTAGE_PHASE_ANGLE.Word_value[1]
27 | 27 | FUXA | ADM100W_1 | ADM100W L2-L3 Voltage | PLC to Client | REAL | LSW | 1 | V | GVL_MODBUS.Input_register_TCP_HMI[26] | GVL_COM.COM_ADM100W_1.SCADA_OUTPUT_L2_L3_VOLTAGE.Word_value[0]
28 | 28 | FUXA | ADM100W_1 | ADM100W L2-L3 Voltage | PLC to Client | REAL | MSW | 1 | V | GVL_MODBUS.Input_register_TCP_HMI[27] | GVL_COM.COM_ADM100W_1.SCADA_OUTPUT_L2_L3_VOLTAGE.Word_value[1]
29 | 29 | FUXA | ADM100W_1 | ADM100W L2-N Voltage | PLC to Client | REAL | LSW | 1 | V | GVL_MODBUS.Input_register_TCP_HMI[28] | GVL_COM.COM_ADM100W_1.SCADA_OUTPUT_L2_N_VOLTAGE.Word_value[0]
30 | 30 | FUXA | ADM100W_1 | ADM100W L2-N Voltage | PLC to Client | REAL | MSW | 1 | V | GVL_MODBUS.Input_register_TCP_HMI[29] | GVL_COM.COM_ADM100W_1.SCADA_OUTPUT_L2_N_VOLTAGE.Word_value[1]
31 | 31 | FUXA | ADM100W_1 | ADM100W L2 Current | PLC to Client | REAL | LSW | 1 | A | GVL_MODBUS.Input_register_TCP_HMI[30] | GVL_COM.COM_ADM100W_1.SCADA_OUTPUT_L2_CURRENT.Word_value[0]
32 | 32 | FUXA | ADM100W_1 | ADM100W L2 Current | PLC to Client | REAL | MSW | 1 | A | GVL_MODBUS.Input_register_TCP_HMI[31] | GVL_COM.COM_ADM100W_1.SCADA_OUTPUT_L2_CURRENT.Word_value[1]
33 | 33 | FUXA | ADM100W_1 | ADM100W L2 Active Power | PLC to Client | REAL | LSW | 1 | per ADM100W config | GVL_MODBUS.Input_register_TCP_HMI[32] | GVL_COM.COM_ADM100W_1.SCADA_OUTPUT_L2_ACTIVE_POWER.Word_value[0]
34 | 34 | FUXA | ADM100W_1 | ADM100W L2 Active Power | PLC to Client | REAL | MSW | 1 | per ADM100W config | GVL_MODBUS.Input_register_TCP_HMI[33] | GVL_COM.COM_ADM100W_1.SCADA_OUTPUT_L2_ACTIVE_POWER.Word_value[1]
35 | 35 | FUXA | ADM100W_1 | ADM100W L2 Apparent Power | PLC to Client | REAL | LSW | 1 | per ADM100W config | GVL_MODBUS.Input_register_TCP_HMI[34] | GVL_COM.COM_ADM100W_1.SCADA_OUTPUT_L2_APPARENT_POWER.Word_value[0]
36 | 36 | FUXA | ADM100W_1 | ADM100W L2 Apparent Power | PLC to Client | REAL | MSW | 1 | per ADM100W config | GVL_MODBUS.Input_register_TCP_HMI[35] | GVL_COM.COM_ADM100W_1.SCADA_OUTPUT_L2_APPARENT_POWER.Word_value[1]
37 | 37 | FUXA | ADM100W_1 | ADM100W L2 Reactive Power | PLC to Client | REAL | LSW | 1 | per ADM100W config | GVL_MODBUS.Input_register_TCP_HMI[36] | GVL_COM.COM_ADM100W_1.SCADA_OUTPUT_L2_REACTIVE_POWER.Word_value[0]
38 | 38 | FUXA | ADM100W_1 | ADM100W L2 Reactive Power | PLC to Client | REAL | MSW | 1 | per ADM100W config | GVL_MODBUS.Input_register_TCP_HMI[37] | GVL_COM.COM_ADM100W_1.SCADA_OUTPUT_L2_REACTIVE_POWER.Word_value[1]
39 | 39 | FUXA | ADM100W_1 | ADM100W L2 Current Phase Angle | PLC to Client | REAL | LSW | 1 | ° | GVL_MODBUS.Input_register_TCP_HMI[38] | GVL_COM.COM_ADM100W_1.SCADA_OUTPUT_L2_CURRENT_PHASE_ANGLE.Word_value[0]
40 | 40 | FUXA | ADM100W_1 | ADM100W L2 Current Phase Angle | PLC to Client | REAL | MSW | 1 | ° | GVL_MODBUS.Input_register_TCP_HMI[39] | GVL_COM.COM_ADM100W_1.SCADA_OUTPUT_L2_CURRENT_PHASE_ANGLE.Word_value[1]
41 | 41 | FUXA | ADM100W_1 | ADM100W L2 Power Factor | PLC to Client | REAL | LSW | 1 |  | GVL_MODBUS.Input_register_TCP_HMI[40] | GVL_COM.COM_ADM100W_1.SCADA_OUTPUT_L2_POWER_FACTOR.Word_value[0]
42 | 42 | FUXA | ADM100W_1 | ADM100W L2 Power Factor | PLC to Client | REAL | MSW | 1 |  | GVL_MODBUS.Input_register_TCP_HMI[41] | GVL_COM.COM_ADM100W_1.SCADA_OUTPUT_L2_POWER_FACTOR.Word_value[1]
43 | 43 | FUXA | ADM100W_1 | ADM100W L2 Voltage THD | PLC to Client | REAL | LSW | 1 | % | GVL_MODBUS.Input_register_TCP_HMI[42] | GVL_COM.COM_ADM100W_1.SCADA_OUTPUT_L2_VOLTAGE_THD.Word_value[0]
44 | 44 | FUXA | ADM100W_1 | ADM100W L2 Voltage THD | PLC to Client | REAL | MSW | 1 | % | GVL_MODBUS.Input_register_TCP_HMI[43] | GVL_COM.COM_ADM100W_1.SCADA_OUTPUT_L2_VOLTAGE_THD.Word_value[1]
45 | 45 | FUXA | ADM100W_1 | ADM100W L2 Current THD | PLC to Client | REAL | LSW | 1 | % | GVL_MODBUS.Input_register_TCP_HMI[44] | GVL_COM.COM_ADM100W_1.SCADA_OUTPUT_L2_CURRENT_THD.Word_value[0]
46 | 46 | FUXA | ADM100W_1 | ADM100W L2 Current THD | PLC to Client | REAL | MSW | 1 | % | GVL_MODBUS.Input_register_TCP_HMI[45] | GVL_COM.COM_ADM100W_1.SCADA_OUTPUT_L2_CURRENT_THD.Word_value[1]
47 | 47 | FUXA | ADM100W_1 | ADM100W L2 Max Load | PLC to Client | REAL | LSW | 1 | per ADM100W config | GVL_MODBUS.Input_register_TCP_HMI[46] | GVL_COM.COM_ADM100W_1.SCADA_OUTPUT_L2_MAX_LOAD.Word_value[0]
48 | 48 | FUXA | ADM100W_1 | ADM100W L2 Max Load | PLC to Client | REAL | MSW | 1 | per ADM100W config | GVL_MODBUS.Input_register_TCP_HMI[47] | GVL_COM.COM_ADM100W_1.SCADA_OUTPUT_L2_MAX_LOAD.Word_value[1]
49 | 49 | FUXA | ADM100W_1 | ADM100W L1-L3 Voltage Phase Angle | PLC to Client | REAL | LSW | 1 | ° | GVL_MODBUS.Input_register_TCP_HMI[48] | GVL_COM.COM_ADM100W_1.SCADA_OUTPUT_L1_L3_VOLTAGE_PHASE_ANGLE.Word_value[0]
50 | 50 | FUXA | ADM100W_1 | ADM100W L1-L3 Voltage Phase Angle | PLC to Client | REAL | MSW | 1 | ° | GVL_MODBUS.Input_register_TCP_HMI[49] | GVL_COM.COM_ADM100W_1.SCADA_OUTPUT_L1_L3_VOLTAGE_PHASE_ANGLE.Word_value[1]
51 | 51 | FUXA | ADM100W_1 | ADM100W L3-L1 Voltage | PLC to Client | REAL | LSW | 1 | V | GVL_MODBUS.Input_register_TCP_HMI[50] | GVL_COM.COM_ADM100W_1.SCADA_OUTPUT_L3_L1_VOLTAGE.Word_value[0]
52 | 52 | FUXA | ADM100W_1 | ADM100W L3-L1 Voltage | PLC to Client | REAL | MSW | 1 | V | GVL_MODBUS.Input_register_TCP_HMI[51] | GVL_COM.COM_ADM100W_1.SCADA_OUTPUT_L3_L1_VOLTAGE.Word_value[1]
53 | 53 | FUXA | ADM100W_1 | ADM100W L3-N Voltage | PLC to Client | REAL | LSW | 1 | V | GVL_MODBUS.Input_register_TCP_HMI[52] | GVL_COM.COM_ADM100W_1.SCADA_OUTPUT_L3_N_VOLTAGE.Word_value[0]
54 | 54 | FUXA | ADM100W_1 | ADM100W L3-N Voltage | PLC to Client | REAL | MSW | 1 | V | GVL_MODBUS.Input_register_TCP_HMI[53] | GVL_COM.COM_ADM100W_1.SCADA_OUTPUT_L3_N_VOLTAGE.Word_value[1]
55 | 55 | FUXA | ADM100W_1 | ADM100W L3 Current | PLC to Client | REAL | LSW | 1 | A | GVL_MODBUS.Input_register_TCP_HMI[54] | GVL_COM.COM_ADM100W_1.SCADA_OUTPUT_L3_CURRENT.Word_value[0]
56 | 56 | FUXA | ADM100W_1 | ADM100W L3 Current | PLC to Client | REAL | MSW | 1 | A | GVL_MODBUS.Input_register_TCP_HMI[55] | GVL_COM.COM_ADM100W_1.SCADA_OUTPUT_L3_CURRENT.Word_value[1]
57 | 57 | FUXA | ADM100W_1 | ADM100W L3 Active Power | PLC to Client | REAL | LSW | 1 | per ADM100W config | GVL_MODBUS.Input_register_TCP_HMI[56] | GVL_COM.COM_ADM100W_1.SCADA_OUTPUT_L3_ACTIVE_POWER.Word_value[0]
58 | 58 | FUXA | ADM100W_1 | ADM100W L3 Active Power | PLC to Client | REAL | MSW | 1 | per ADM100W config | GVL_MODBUS.Input_register_TCP_HMI[57] | GVL_COM.COM_ADM100W_1.SCADA_OUTPUT_L3_ACTIVE_POWER.Word_value[1]
59 | 59 | FUXA | ADM100W_1 | ADM100W L3 Apparent Power | PLC to Client | REAL | LSW | 1 | per ADM100W config | GVL_MODBUS.Input_register_TCP_HMI[58] | GVL_COM.COM_ADM100W_1.SCADA_OUTPUT_L3_APPARENT_POWER.Word_value[0]
60 | 60 | FUXA | ADM100W_1 | ADM100W L3 Apparent Power | PLC to Client | REAL | MSW | 1 | per ADM100W config | GVL_MODBUS.Input_register_TCP_HMI[59] | GVL_COM.COM_ADM100W_1.SCADA_OUTPUT_L3_APPARENT_POWER.Word_value[1]
61 | 61 | FUXA | ADM100W_1 | ADM100W L3 Reactive Power | PLC to Client | REAL | LSW | 1 | per ADM100W config | GVL_MODBUS.Input_register_TCP_HMI[60] | GVL_COM.COM_ADM100W_1.SCADA_OUTPUT_L3_REACTIVE_POWER.Word_value[0]
62 | 62 | FUXA | ADM100W_1 | ADM100W L3 Reactive Power | PLC to Client | REAL | MSW | 1 | per ADM100W config | GVL_MODBUS.Input_register_TCP_HMI[61] | GVL_COM.COM_ADM100W_1.SCADA_OUTPUT_L3_REACTIVE_POWER.Word_value[1]
63 | 63 | FUXA | ADM100W_1 | ADM100W L3 Current Phase Angle | PLC to Client | REAL | LSW | 1 | ° | GVL_MODBUS.Input_register_TCP_HMI[62] | GVL_COM.COM_ADM100W_1.SCADA_OUTPUT_L3_CURRENT_PHASE_ANGLE.Word_value[0]
64 | 64 | FUXA | ADM100W_1 | ADM100W L3 Current Phase Angle | PLC to Client | REAL | MSW | 1 | ° | GVL_MODBUS.Input_register_TCP_HMI[63] | GVL_COM.COM_ADM100W_1.SCADA_OUTPUT_L3_CURRENT_PHASE_ANGLE.Word_value[1]
65 | 65 | FUXA | ADM100W_1 | ADM100W L3 Power Factor | PLC to Client | REAL | LSW | 1 |  | GVL_MODBUS.Input_register_TCP_HMI[64] | GVL_COM.COM_ADM100W_1.SCADA_OUTPUT_L3_POWER_FACTOR.Word_value[0]
66 | 66 | FUXA | ADM100W_1 | ADM100W L3 Power Factor | PLC to Client | REAL | MSW | 1 |  | GVL_MODBUS.Input_register_TCP_HMI[65] | GVL_COM.COM_ADM100W_1.SCADA_OUTPUT_L3_POWER_FACTOR.Word_value[1]
67 | 67 | FUXA | ADM100W_1 | ADM100W L3 Voltage THD | PLC to Client | REAL | LSW | 1 | % | GVL_MODBUS.Input_register_TCP_HMI[66] | GVL_COM.COM_ADM100W_1.SCADA_OUTPUT_L3_VOLTAGE_THD.Word_value[0]
68 | 68 | FUXA | ADM100W_1 | ADM100W L3 Voltage THD | PLC to Client | REAL | MSW | 1 | % | GVL_MODBUS.Input_register_TCP_HMI[67] | GVL_COM.COM_ADM100W_1.SCADA_OUTPUT_L3_VOLTAGE_THD.Word_value[1]
69 | 69 | FUXA | ADM100W_1 | ADM100W L3 Current THD | PLC to Client | REAL | LSW | 1 | % | GVL_MODBUS.Input_register_TCP_HMI[68] | GVL_COM.COM_ADM100W_1.SCADA_OUTPUT_L3_CURRENT_THD.Word_value[0]
70 | 70 | FUXA | ADM100W_1 | ADM100W L3 Current THD | PLC to Client | REAL | MSW | 1 | % | GVL_MODBUS.Input_register_TCP_HMI[69] | GVL_COM.COM_ADM100W_1.SCADA_OUTPUT_L3_CURRENT_THD.Word_value[1]
71 | 71 | FUXA | ADM100W_1 | ADM100W L3 Max Load | PLC to Client | REAL | LSW | 1 | per ADM100W config | GVL_MODBUS.Input_register_TCP_HMI[70] | GVL_COM.COM_ADM100W_1.SCADA_OUTPUT_L3_MAX_LOAD.Word_value[0]
72 | 72 | FUXA | ADM100W_1 | ADM100W L3 Max Load | PLC to Client | REAL | MSW | 1 | per ADM100W config | GVL_MODBUS.Input_register_TCP_HMI[71] | GVL_COM.COM_ADM100W_1.SCADA_OUTPUT_L3_MAX_LOAD.Word_value[1]
73 | 73 | FUXA | ADM100W_1 | ADM100W Internal Temperature | PLC to Client | REAL | LSW | 1 | per ADM100W config | GVL_MODBUS.Input_register_TCP_HMI[72] | GVL_COM.COM_ADM100W_1.SCADA_OUTPUT_INTERNAL_TEMPERATURE.Word_value[0]
74 | 74 | FUXA | ADM100W_1 | ADM100W Internal Temperature | PLC to Client | REAL | MSW | 1 | per ADM100W config | GVL_MODBUS.Input_register_TCP_HMI[73] | GVL_COM.COM_ADM100W_1.SCADA_OUTPUT_INTERNAL_TEMPERATURE.Word_value[1]
75 | 75 | FUXA | ADM100W_1 | ADM100W Active Energy | PLC to Client | REAL | LSW | 1 | per ADM100W config | GVL_MODBUS.Input_register_TCP_HMI[74] | GVL_COM.COM_ADM100W_1.SCADA_OUTPUT_ACTIVE_ENERGY.Word_value[0]
76 | 76 | FUXA | ADM100W_1 | ADM100W Active Energy | PLC to Client | REAL | MSW | 1 | per ADM100W config | GVL_MODBUS.Input_register_TCP_HMI[75] | GVL_COM.COM_ADM100W_1.SCADA_OUTPUT_ACTIVE_ENERGY.Word_value[1]
77 | 77 | FUXA | ADM100W_1 | ADM100W Apparent Energy | PLC to Client | REAL | LSW | 1 | per ADM100W config | GVL_MODBUS.Input_register_TCP_HMI[76] | GVL_COM.COM_ADM100W_1.SCADA_OUTPUT_APPARENT_ENERGY.Word_value[0]
78 | 78 | FUXA | ADM100W_1 | ADM100W Apparent Energy | PLC to Client | REAL | MSW | 1 | per ADM100W config | GVL_MODBUS.Input_register_TCP_HMI[77] | GVL_COM.COM_ADM100W_1.SCADA_OUTPUT_APPARENT_ENERGY.Word_value[1]
79 | 79 | FUXA | ADM100W_1 | ADM100W Reactive Energy | PLC to Client | REAL | LSW | 1 | per ADM100W config | GVL_MODBUS.Input_register_TCP_HMI[78] | GVL_COM.COM_ADM100W_1.SCADA_OUTPUT_REACTIVE_ENERGY.Word_value[0]
80 | 80 | FUXA | ADM100W_1 | ADM100W Reactive Energy | PLC to Client | REAL | MSW | 1 | per ADM100W config | GVL_MODBUS.Input_register_TCP_HMI[79] | GVL_COM.COM_ADM100W_1.SCADA_OUTPUT_REACTIVE_ENERGY.Word_value[1]
81 | 81 | FUXA | ADM100W_1 | ADM100W Total Active Power | PLC to Client | REAL | LSW | 1 | per ADM100W config | GVL_MODBUS.Input_register_TCP_HMI[80] | GVL_COM.COM_ADM100W_1.SCADA_OUTPUT_TOTAL_ACTIVE_POWER.Word_value[0]
82 | 82 | FUXA | ADM100W_1 | ADM100W Total Active Power | PLC to Client | REAL | MSW | 1 | per ADM100W config | GVL_MODBUS.Input_register_TCP_HMI[81] | GVL_COM.COM_ADM100W_1.SCADA_OUTPUT_TOTAL_ACTIVE_POWER.Word_value[1]
83 | 83 | FUXA | ADM100W_1 | ADM100W Total Apparent Power | PLC to Client | REAL | LSW | 1 | per ADM100W config | GVL_MODBUS.Input_register_TCP_HMI[82] | GVL_COM.COM_ADM100W_1.SCADA_OUTPUT_TOTAL_APPARENT_POWER.Word_value[0]
84 | 84 | FUXA | ADM100W_1 | ADM100W Total Apparent Power | PLC to Client | REAL | MSW | 1 | per ADM100W config | GVL_MODBUS.Input_register_TCP_HMI[83] | GVL_COM.COM_ADM100W_1.SCADA_OUTPUT_TOTAL_APPARENT_POWER.Word_value[1]
85 | 85 | FUXA | ADM100W_1 | ADM100W Total Reactive Power | PLC to Client | REAL | LSW | 1 | per ADM100W config | GVL_MODBUS.Input_register_TCP_HMI[84] | GVL_COM.COM_ADM100W_1.SCADA_OUTPUT_TOTAL_REACTIVE_POWER.Word_value[0]
86 | 86 | FUXA | ADM100W_1 | ADM100W Total Reactive Power | PLC to Client | REAL | MSW | 1 | per ADM100W config | GVL_MODBUS.Input_register_TCP_HMI[85] | GVL_COM.COM_ADM100W_1.SCADA_OUTPUT_TOTAL_REACTIVE_POWER.Word_value[1]
87 | 87 | FUXA | ADM100W_1 | ADM100W All Phase Power Factor | PLC to Client | REAL | LSW | 1 |  | GVL_MODBUS.Input_register_TCP_HMI[86] | GVL_COM.COM_ADM100W_1.SCADA_OUTPUT_ALL_PHASE_POWER_FACTOR.Word_value[0]
88 | 88 | FUXA | ADM100W_1 | ADM100W All Phase Power Factor | PLC to Client | REAL | MSW | 1 |  | GVL_MODBUS.Input_register_TCP_HMI[87] | GVL_COM.COM_ADM100W_1.SCADA_OUTPUT_ALL_PHASE_POWER_FACTOR.Word_value[1]
89 | 89 | FUXA | DOSENSOR_1 | DO Sensor Signal | PLC to Client | REAL | LSW | 1 |  | GVL_MODBUS.Input_register_TCP_HMI[88] | GVL_COM.COM_DOSENSOR_1.SCADA_OUTPUT_SIGNAL.Word_value[0]
90 | 90 | FUXA | DOSENSOR_1 | DO Sensor Signal | PLC to Client | REAL | MSW | 1 |  | GVL_MODBUS.Input_register_TCP_HMI[89] | GVL_COM.COM_DOSENSOR_1.SCADA_OUTPUT_SIGNAL.Word_value[1]
91 | 91 | FUXA | DIP1500_1 | DIP1500 Firmware Version | PLC to Client | WORD |  | 3+5+8 bits (major+minor+revision) |  | GVL_MODBUS.Input_register_TCP_HMI[90] | GVL_COM.COM_DIP1500_1.SCADA_OUTPUT_FIRMWARE_VERSION
92 | 92 | FUXA | DIP1500_1 | DIP1500 Hardware Version | PLC to Client | WORD |  | 3+5+8 bits (major+minor+revision) |  | GVL_MODBUS.Input_register_TCP_HMI[91] | GVL_COM.COM_DIP1500_1.SCADA_OUTPUT_HARDWARE_VERSION
93 | 93 | FUXA | DIP1500_1 | DIP1500 Temperature | PLC to Client | WORD |  | (raw - 500) / 10 | °C | GVL_MODBUS.Input_register_TCP_HMI[92] | GVL_COM.COM_DIP1500_1.SCADA_OUTPUT_TEMPERATURE
94 | 94 | FUXA | DIP1500_1 | DIP1500 Float Level Alarm | PLC to Client | WORD |  | 1 |  | GVL_MODBUS.Input_register_TCP_HMI[93] | GVL_COM.COM_DIP1500_1.SCADA_OUTPUT_FLOAT_LEVEL_ALARM
95 | 95 | FUXA | DIP1500_1 | DIP1500 Digital Output Value | PLC to Client | WORD |  | 1 |  | GVL_MODBUS.Input_register_TCP_HMI[94] | GVL_COM.COM_DIP1500_1.SCADA_OUTPUT_DIGITAL_OUTPUT_VALUE
96 | 96 | FUXA | DIP1500_1 | DIP1500 Real-Time Run Time Or Volume | PLC to Client | REAL | LSW | 1 | ms (time mode) / ml (volume mode) | GVL_MODBUS.Input_register_TCP_HMI[95] | GVL_COM.COM_DIP1500_1.SCADA_OUTPUT_REAL_TIME_RUN_TIME_OR_VOLUME.Word_value[0]
97 | 97 | FUXA | DIP1500_1 | DIP1500 Real-Time Run Time Or Volume | PLC to Client | REAL | MSW | 1 | ms (time mode) / ml (volume mode) | GVL_MODBUS.Input_register_TCP_HMI[96] | GVL_COM.COM_DIP1500_1.SCADA_OUTPUT_REAL_TIME_RUN_TIME_OR_VOLUME.Word_value[1]
98 | 98 | FUXA | DIP1500_1 | DIP1500 Accumulated Run Time Or Volume | PLC to Client | REAL | LSW | 1 | ms (time mode) / ml (volume mode) | GVL_MODBUS.Input_register_TCP_HMI[97] | GVL_COM.COM_DIP1500_1.SCADA_OUTPUT_ACCUMULATED_RUN_TIME_OR_VOLUME.Word_value[0]
99 | 99 | FUXA | DIP1500_1 | DIP1500 Accumulated Run Time Or Volume | PLC to Client | REAL | MSW | 1 | ms (time mode) / ml (volume mode) | GVL_MODBUS.Input_register_TCP_HMI[98] | GVL_COM.COM_DIP1500_1.SCADA_OUTPUT_ACCUMULATED_RUN_TIME_OR_VOLUME.Word_value[1]
1001 | 1001 | HMI | ADM100W_1 | ADM100W Frequency | PLC to Client | REAL | LSW | 1 | Hz | GVL_MODBUS.Input_register_TCP_HMI[1000] | GVL_COM.COM_ADM100W_1.HMI_OUTPUT_FREQUENCY.Word_value[0]
1002 | 1002 | HMI | ADM100W_1 | ADM100W Frequency | PLC to Client | REAL | MSW | 1 | Hz | GVL_MODBUS.Input_register_TCP_HMI[1001] | GVL_COM.COM_ADM100W_1.HMI_OUTPUT_FREQUENCY.Word_value[1]
1003 | 1003 | HMI | ADM100W_1 | ADM100W L1-L2 Voltage | PLC to Client | REAL | LSW | 1 | V | GVL_MODBUS.Input_register_TCP_HMI[1002] | GVL_COM.COM_ADM100W_1.HMI_OUTPUT_L1_L2_VOLTAGE.Word_value[0]
1004 | 1004 | HMI | ADM100W_1 | ADM100W L1-L2 Voltage | PLC to Client | REAL | MSW | 1 | V | GVL_MODBUS.Input_register_TCP_HMI[1003] | GVL_COM.COM_ADM100W_1.HMI_OUTPUT_L1_L2_VOLTAGE.Word_value[1]
1005 | 1005 | HMI | ADM100W_1 | ADM100W L1-N Voltage | PLC to Client | REAL | LSW | 1 | V | GVL_MODBUS.Input_register_TCP_HMI[1004] | GVL_COM.COM_ADM100W_1.HMI_OUTPUT_L1_N_VOLTAGE.Word_value[0]
1006 | 1006 | HMI | ADM100W_1 | ADM100W L1-N Voltage | PLC to Client | REAL | MSW | 1 | V | GVL_MODBUS.Input_register_TCP_HMI[1005] | GVL_COM.COM_ADM100W_1.HMI_OUTPUT_L1_N_VOLTAGE.Word_value[1]
1007 | 1007 | HMI | ADM100W_1 | ADM100W L1 Current | PLC to Client | REAL | LSW | 1 | A | GVL_MODBUS.Input_register_TCP_HMI[1006] | GVL_COM.COM_ADM100W_1.HMI_OUTPUT_L1_CURRENT.Word_value[0]
1008 | 1008 | HMI | ADM100W_1 | ADM100W L1 Current | PLC to Client | REAL | MSW | 1 | A | GVL_MODBUS.Input_register_TCP_HMI[1007] | GVL_COM.COM_ADM100W_1.HMI_OUTPUT_L1_CURRENT.Word_value[1]
1009 | 1009 | HMI | ADM100W_1 | ADM100W L1 Active Power | PLC to Client | REAL | LSW | 1 | per ADM100W config | GVL_MODBUS.Input_register_TCP_HMI[1008] | GVL_COM.COM_ADM100W_1.HMI_OUTPUT_L1_ACTIVE_POWER.Word_value[0]
1010 | 1010 | HMI | ADM100W_1 | ADM100W L1 Active Power | PLC to Client | REAL | MSW | 1 | per ADM100W config | GVL_MODBUS.Input_register_TCP_HMI[1009] | GVL_COM.COM_ADM100W_1.HMI_OUTPUT_L1_ACTIVE_POWER.Word_value[1]
1011 | 1011 | HMI | ADM100W_1 | ADM100W L1 Apparent Power | PLC to Client | REAL | LSW | 1 | per ADM100W config | GVL_MODBUS.Input_register_TCP_HMI[1010] | GVL_COM.COM_ADM100W_1.HMI_OUTPUT_L1_APPARENT_POWER.Word_value[0]
1012 | 1012 | HMI | ADM100W_1 | ADM100W L1 Apparent Power | PLC to Client | REAL | MSW | 1 | per ADM100W config | GVL_MODBUS.Input_register_TCP_HMI[1011] | GVL_COM.COM_ADM100W_1.HMI_OUTPUT_L1_APPARENT_POWER.Word_value[1]
1013 | 1013 | HMI | ADM100W_1 | ADM100W L1 Reactive Power | PLC to Client | REAL | LSW | 1 | per ADM100W config | GVL_MODBUS.Input_register_TCP_HMI[1012] | GVL_COM.COM_ADM100W_1.HMI_OUTPUT_L1_REACTIVE_POWER.Word_value[0]
1014 | 1014 | HMI | ADM100W_1 | ADM100W L1 Reactive Power | PLC to Client | REAL | MSW | 1 | per ADM100W config | GVL_MODBUS.Input_register_TCP_HMI[1013] | GVL_COM.COM_ADM100W_1.HMI_OUTPUT_L1_REACTIVE_POWER.Word_value[1]
1015 | 1015 | HMI | ADM100W_1 | ADM100W L1 Current Phase Angle | PLC to Client | REAL | LSW | 1 | ° | GVL_MODBUS.Input_register_TCP_HMI[1014] | GVL_COM.COM_ADM100W_1.HMI_OUTPUT_L1_CURRENT_PHASE_ANGLE.Word_value[0]
1016 | 1016 | HMI | ADM100W_1 | ADM100W L1 Current Phase Angle | PLC to Client | REAL | MSW | 1 | ° | GVL_MODBUS.Input_register_TCP_HMI[1015] | GVL_COM.COM_ADM100W_1.HMI_OUTPUT_L1_CURRENT_PHASE_ANGLE.Word_value[1]
1017 | 1017 | HMI | ADM100W_1 | ADM100W L1 Power Factor | PLC to Client | REAL | LSW | 1 |  | GVL_MODBUS.Input_register_TCP_HMI[1016] | GVL_COM.COM_ADM100W_1.HMI_OUTPUT_L1_POWER_FACTOR.Word_value[0]
1018 | 1018 | HMI | ADM100W_1 | ADM100W L1 Power Factor | PLC to Client | REAL | MSW | 1 |  | GVL_MODBUS.Input_register_TCP_HMI[1017] | GVL_COM.COM_ADM100W_1.HMI_OUTPUT_L1_POWER_FACTOR.Word_value[1]
1019 | 1019 | HMI | ADM100W_1 | ADM100W L1 Voltage THD | PLC to Client | REAL | LSW | 1 | % | GVL_MODBUS.Input_register_TCP_HMI[1018] | GVL_COM.COM_ADM100W_1.HMI_OUTPUT_L1_VOLTAGE_THD.Word_value[0]
1020 | 1020 | HMI | ADM100W_1 | ADM100W L1 Voltage THD | PLC to Client | REAL | MSW | 1 | % | GVL_MODBUS.Input_register_TCP_HMI[1019] | GVL_COM.COM_ADM100W_1.HMI_OUTPUT_L1_VOLTAGE_THD.Word_value[1]
1021 | 1021 | HMI | ADM100W_1 | ADM100W L1 Current THD | PLC to Client | REAL | LSW | 1 | % | GVL_MODBUS.Input_register_TCP_HMI[1020] | GVL_COM.COM_ADM100W_1.HMI_OUTPUT_L1_CURRENT_THD.Word_value[0]
1022 | 1022 | HMI | ADM100W_1 | ADM100W L1 Current THD | PLC to Client | REAL | MSW | 1 | % | GVL_MODBUS.Input_register_TCP_HMI[1021] | GVL_COM.COM_ADM100W_1.HMI_OUTPUT_L1_CURRENT_THD.Word_value[1]
1023 | 1023 | HMI | ADM100W_1 | ADM100W L1 Max Load | PLC to Client | REAL | LSW | 1 | per ADM100W config | GVL_MODBUS.Input_register_TCP_HMI[1022] | GVL_COM.COM_ADM100W_1.HMI_OUTPUT_L1_MAX_LOAD.Word_value[0]
1024 | 1024 | HMI | ADM100W_1 | ADM100W L1 Max Load | PLC to Client | REAL | MSW | 1 | per ADM100W config | GVL_MODBUS.Input_register_TCP_HMI[1023] | GVL_COM.COM_ADM100W_1.HMI_OUTPUT_L1_MAX_LOAD.Word_value[1]
1025 | 1025 | HMI | ADM100W_1 | ADM100W L1-L2 Voltage Phase Angle | PLC to Client | REAL | LSW | 1 | ° | GVL_MODBUS.Input_register_TCP_HMI[1024] | GVL_COM.COM_ADM100W_1.HMI_OUTPUT_L1_L2_VOLTAGE_PHASE_ANGLE.Word_value[0]
1026 | 1026 | HMI | ADM100W_1 | ADM100W L1-L2 Voltage Phase Angle | PLC to Client | REAL | MSW | 1 | ° | GVL_MODBUS.Input_register_TCP_HMI[1025] | GVL_COM.COM_ADM100W_1.HMI_OUTPUT_L1_L2_VOLTAGE_PHASE_ANGLE.Word_value[1]
1027 | 1027 | HMI | ADM100W_1 | ADM100W L2-L3 Voltage | PLC to Client | REAL | LSW | 1 | V | GVL_MODBUS.Input_register_TCP_HMI[1026] | GVL_COM.COM_ADM100W_1.HMI_OUTPUT_L2_L3_VOLTAGE.Word_value[0]
1028 | 1028 | HMI | ADM100W_1 | ADM100W L2-L3 Voltage | PLC to Client | REAL | MSW | 1 | V | GVL_MODBUS.Input_register_TCP_HMI[1027] | GVL_COM.COM_ADM100W_1.HMI_OUTPUT_L2_L3_VOLTAGE.Word_value[1]
1029 | 1029 | HMI | ADM100W_1 | ADM100W L2-N Voltage | PLC to Client | REAL | LSW | 1 | V | GVL_MODBUS.Input_register_TCP_HMI[1028] | GVL_COM.COM_ADM100W_1.HMI_OUTPUT_L2_N_VOLTAGE.Word_value[0]
1030 | 1030 | HMI | ADM100W_1 | ADM100W L2-N Voltage | PLC to Client | REAL | MSW | 1 | V | GVL_MODBUS.Input_register_TCP_HMI[1029] | GVL_COM.COM_ADM100W_1.HMI_OUTPUT_L2_N_VOLTAGE.Word_value[1]
1031 | 1031 | HMI | ADM100W_1 | ADM100W L2 Current | PLC to Client | REAL | LSW | 1 | A | GVL_MODBUS.Input_register_TCP_HMI[1030] | GVL_COM.COM_ADM100W_1.HMI_OUTPUT_L2_CURRENT.Word_value[0]
1032 | 1032 | HMI | ADM100W_1 | ADM100W L2 Current | PLC to Client | REAL | MSW | 1 | A | GVL_MODBUS.Input_register_TCP_HMI[1031] | GVL_COM.COM_ADM100W_1.HMI_OUTPUT_L2_CURRENT.Word_value[1]
1033 | 1033 | HMI | ADM100W_1 | ADM100W L2 Active Power | PLC to Client | REAL | LSW | 1 | per ADM100W config | GVL_MODBUS.Input_register_TCP_HMI[1032] | GVL_COM.COM_ADM100W_1.HMI_OUTPUT_L2_ACTIVE_POWER.Word_value[0]
1034 | 1034 | HMI | ADM100W_1 | ADM100W L2 Active Power | PLC to Client | REAL | MSW | 1 | per ADM100W config | GVL_MODBUS.Input_register_TCP_HMI[1033] | GVL_COM.COM_ADM100W_1.HMI_OUTPUT_L2_ACTIVE_POWER.Word_value[1]
1035 | 1035 | HMI | ADM100W_1 | ADM100W L2 Apparent Power | PLC to Client | REAL | LSW | 1 | per ADM100W config | GVL_MODBUS.Input_register_TCP_HMI[1034] | GVL_COM.COM_ADM100W_1.HMI_OUTPUT_L2_APPARENT_POWER.Word_value[0]
1036 | 1036 | HMI | ADM100W_1 | ADM100W L2 Apparent Power | PLC to Client | REAL | MSW | 1 | per ADM100W config | GVL_MODBUS.Input_register_TCP_HMI[1035] | GVL_COM.COM_ADM100W_1.HMI_OUTPUT_L2_APPARENT_POWER.Word_value[1]
1037 | 1037 | HMI | ADM100W_1 | ADM100W L2 Reactive Power | PLC to Client | REAL | LSW | 1 | per ADM100W config | GVL_MODBUS.Input_register_TCP_HMI[1036] | GVL_COM.COM_ADM100W_1.HMI_OUTPUT_L2_REACTIVE_POWER.Word_value[0]
1038 | 1038 | HMI | ADM100W_1 | ADM100W L2 Reactive Power | PLC to Client | REAL | MSW | 1 | per ADM100W config | GVL_MODBUS.Input_register_TCP_HMI[1037] | GVL_COM.COM_ADM100W_1.HMI_OUTPUT_L2_REACTIVE_POWER.Word_value[1]
1039 | 1039 | HMI | ADM100W_1 | ADM100W L2 Current Phase Angle | PLC to Client | REAL | LSW | 1 | ° | GVL_MODBUS.Input_register_TCP_HMI[1038] | GVL_COM.COM_ADM100W_1.HMI_OUTPUT_L2_CURRENT_PHASE_ANGLE.Word_value[0]
1040 | 1040 | HMI | ADM100W_1 | ADM100W L2 Current Phase Angle | PLC to Client | REAL | MSW | 1 | ° | GVL_MODBUS.Input_register_TCP_HMI[1039] | GVL_COM.COM_ADM100W_1.HMI_OUTPUT_L2_CURRENT_PHASE_ANGLE.Word_value[1]
1041 | 1041 | HMI | ADM100W_1 | ADM100W L2 Power Factor | PLC to Client | REAL | LSW | 1 |  | GVL_MODBUS.Input_register_TCP_HMI[1040] | GVL_COM.COM_ADM100W_1.HMI_OUTPUT_L2_POWER_FACTOR.Word_value[0]
1042 | 1042 | HMI | ADM100W_1 | ADM100W L2 Power Factor | PLC to Client | REAL | MSW | 1 |  | GVL_MODBUS.Input_register_TCP_HMI[1041] | GVL_COM.COM_ADM100W_1.HMI_OUTPUT_L2_POWER_FACTOR.Word_value[1]
1043 | 1043 | HMI | ADM100W_1 | ADM100W L2 Voltage THD | PLC to Client | REAL | LSW | 1 | % | GVL_MODBUS.Input_register_TCP_HMI[1042] | GVL_COM.COM_ADM100W_1.HMI_OUTPUT_L2_VOLTAGE_THD.Word_value[0]
1044 | 1044 | HMI | ADM100W_1 | ADM100W L2 Voltage THD | PLC to Client | REAL | MSW | 1 | % | GVL_MODBUS.Input_register_TCP_HMI[1043] | GVL_COM.COM_ADM100W_1.HMI_OUTPUT_L2_VOLTAGE_THD.Word_value[1]
1045 | 1045 | HMI | ADM100W_1 | ADM100W L2 Current THD | PLC to Client | REAL | LSW | 1 | % | GVL_MODBUS.Input_register_TCP_HMI[1044] | GVL_COM.COM_ADM100W_1.HMI_OUTPUT_L2_CURRENT_THD.Word_value[0]
1046 | 1046 | HMI | ADM100W_1 | ADM100W L2 Current THD | PLC to Client | REAL | MSW | 1 | % | GVL_MODBUS.Input_register_TCP_HMI[1045] | GVL_COM.COM_ADM100W_1.HMI_OUTPUT_L2_CURRENT_THD.Word_value[1]
1047 | 1047 | HMI | ADM100W_1 | ADM100W L2 Max Load | PLC to Client | REAL | LSW | 1 | per ADM100W config | GVL_MODBUS.Input_register_TCP_HMI[1046] | GVL_COM.COM_ADM100W_1.HMI_OUTPUT_L2_MAX_LOAD.Word_value[0]
1048 | 1048 | HMI | ADM100W_1 | ADM100W L2 Max Load | PLC to Client | REAL | MSW | 1 | per ADM100W config | GVL_MODBUS.Input_register_TCP_HMI[1047] | GVL_COM.COM_ADM100W_1.HMI_OUTPUT_L2_MAX_LOAD.Word_value[1]
1049 | 1049 | HMI | ADM100W_1 | ADM100W L1-L3 Voltage Phase Angle | PLC to Client | REAL | LSW | 1 | ° | GVL_MODBUS.Input_register_TCP_HMI[1048] | GVL_COM.COM_ADM100W_1.HMI_OUTPUT_L1_L3_VOLTAGE_PHASE_ANGLE.Word_value[0]
1050 | 1050 | HMI | ADM100W_1 | ADM100W L1-L3 Voltage Phase Angle | PLC to Client | REAL | MSW | 1 | ° | GVL_MODBUS.Input_register_TCP_HMI[1049] | GVL_COM.COM_ADM100W_1.HMI_OUTPUT_L1_L3_VOLTAGE_PHASE_ANGLE.Word_value[1]
1051 | 1051 | HMI | ADM100W_1 | ADM100W L3-L1 Voltage | PLC to Client | REAL | LSW | 1 | V | GVL_MODBUS.Input_register_TCP_HMI[1050] | GVL_COM.COM_ADM100W_1.HMI_OUTPUT_L3_L1_VOLTAGE.Word_value[0]
1052 | 1052 | HMI | ADM100W_1 | ADM100W L3-L1 Voltage | PLC to Client | REAL | MSW | 1 | V | GVL_MODBUS.Input_register_TCP_HMI[1051] | GVL_COM.COM_ADM100W_1.HMI_OUTPUT_L3_L1_VOLTAGE.Word_value[1]
1053 | 1053 | HMI | ADM100W_1 | ADM100W L3-N Voltage | PLC to Client | REAL | LSW | 1 | V | GVL_MODBUS.Input_register_TCP_HMI[1052] | GVL_COM.COM_ADM100W_1.HMI_OUTPUT_L3_N_VOLTAGE.Word_value[0]
1054 | 1054 | HMI | ADM100W_1 | ADM100W L3-N Voltage | PLC to Client | REAL | MSW | 1 | V | GVL_MODBUS.Input_register_TCP_HMI[1053] | GVL_COM.COM_ADM100W_1.HMI_OUTPUT_L3_N_VOLTAGE.Word_value[1]
1055 | 1055 | HMI | ADM100W_1 | ADM100W L3 Current | PLC to Client | REAL | LSW | 1 | A | GVL_MODBUS.Input_register_TCP_HMI[1054] | GVL_COM.COM_ADM100W_1.HMI_OUTPUT_L3_CURRENT.Word_value[0]
1056 | 1056 | HMI | ADM100W_1 | ADM100W L3 Current | PLC to Client | REAL | MSW | 1 | A | GVL_MODBUS.Input_register_TCP_HMI[1055] | GVL_COM.COM_ADM100W_1.HMI_OUTPUT_L3_CURRENT.Word_value[1]
1057 | 1057 | HMI | ADM100W_1 | ADM100W L3 Active Power | PLC to Client | REAL | LSW | 1 | per ADM100W config | GVL_MODBUS.Input_register_TCP_HMI[1056] | GVL_COM.COM_ADM100W_1.HMI_OUTPUT_L3_ACTIVE_POWER.Word_value[0]
1058 | 1058 | HMI | ADM100W_1 | ADM100W L3 Active Power | PLC to Client | REAL | MSW | 1 | per ADM100W config | GVL_MODBUS.Input_register_TCP_HMI[1057] | GVL_COM.COM_ADM100W_1.HMI_OUTPUT_L3_ACTIVE_POWER.Word_value[1]
1059 | 1059 | HMI | ADM100W_1 | ADM100W L3 Apparent Power | PLC to Client | REAL | LSW | 1 | per ADM100W config | GVL_MODBUS.Input_register_TCP_HMI[1058] | GVL_COM.COM_ADM100W_1.HMI_OUTPUT_L3_APPARENT_POWER.Word_value[0]
1060 | 1060 | HMI | ADM100W_1 | ADM100W L3 Apparent Power | PLC to Client | REAL | MSW | 1 | per ADM100W config | GVL_MODBUS.Input_register_TCP_HMI[1059] | GVL_COM.COM_ADM100W_1.HMI_OUTPUT_L3_APPARENT_POWER.Word_value[1]
1061 | 1061 | HMI | ADM100W_1 | ADM100W L3 Reactive Power | PLC to Client | REAL | LSW | 1 | per ADM100W config | GVL_MODBUS.Input_register_TCP_HMI[1060] | GVL_COM.COM_ADM100W_1.HMI_OUTPUT_L3_REACTIVE_POWER.Word_value[0]
1062 | 1062 | HMI | ADM100W_1 | ADM100W L3 Reactive Power | PLC to Client | REAL | MSW | 1 | per ADM100W config | GVL_MODBUS.Input_register_TCP_HMI[1061] | GVL_COM.COM_ADM100W_1.HMI_OUTPUT_L3_REACTIVE_POWER.Word_value[1]
1063 | 1063 | HMI | ADM100W_1 | ADM100W L3 Current Phase Angle | PLC to Client | REAL | LSW | 1 | ° | GVL_MODBUS.Input_register_TCP_HMI[1062] | GVL_COM.COM_ADM100W_1.HMI_OUTPUT_L3_CURRENT_PHASE_ANGLE.Word_value[0]
1064 | 1064 | HMI | ADM100W_1 | ADM100W L3 Current Phase Angle | PLC to Client | REAL | MSW | 1 | ° | GVL_MODBUS.Input_register_TCP_HMI[1063] | GVL_COM.COM_ADM100W_1.HMI_OUTPUT_L3_CURRENT_PHASE_ANGLE.Word_value[1]
1065 | 1065 | HMI | ADM100W_1 | ADM100W L3 Power Factor | PLC to Client | REAL | LSW | 1 |  | GVL_MODBUS.Input_register_TCP_HMI[1064] | GVL_COM.COM_ADM100W_1.HMI_OUTPUT_L3_POWER_FACTOR.Word_value[0]
1066 | 1066 | HMI | ADM100W_1 | ADM100W L3 Power Factor | PLC to Client | REAL | MSW | 1 |  | GVL_MODBUS.Input_register_TCP_HMI[1065] | GVL_COM.COM_ADM100W_1.HMI_OUTPUT_L3_POWER_FACTOR.Word_value[1]
1067 | 1067 | HMI | ADM100W_1 | ADM100W L3 Voltage THD | PLC to Client | REAL | LSW | 1 | % | GVL_MODBUS.Input_register_TCP_HMI[1066] | GVL_COM.COM_ADM100W_1.HMI_OUTPUT_L3_VOLTAGE_THD.Word_value[0]
1068 | 1068 | HMI | ADM100W_1 | ADM100W L3 Voltage THD | PLC to Client | REAL | MSW | 1 | % | GVL_MODBUS.Input_register_TCP_HMI[1067] | GVL_COM.COM_ADM100W_1.HMI_OUTPUT_L3_VOLTAGE_THD.Word_value[1]
1069 | 1069 | HMI | ADM100W_1 | ADM100W L3 Current THD | PLC to Client | REAL | LSW | 1 | % | GVL_MODBUS.Input_register_TCP_HMI[1068] | GVL_COM.COM_ADM100W_1.HMI_OUTPUT_L3_CURRENT_THD.Word_value[0]
1070 | 1070 | HMI | ADM100W_1 | ADM100W L3 Current THD | PLC to Client | REAL | MSW | 1 | % | GVL_MODBUS.Input_register_TCP_HMI[1069] | GVL_COM.COM_ADM100W_1.HMI_OUTPUT_L3_CURRENT_THD.Word_value[1]
1071 | 1071 | HMI | ADM100W_1 | ADM100W L3 Max Load | PLC to Client | REAL | LSW | 1 | per ADM100W config | GVL_MODBUS.Input_register_TCP_HMI[1070] | GVL_COM.COM_ADM100W_1.HMI_OUTPUT_L3_MAX_LOAD.Word_value[0]
1072 | 1072 | HMI | ADM100W_1 | ADM100W L3 Max Load | PLC to Client | REAL | MSW | 1 | per ADM100W config | GVL_MODBUS.Input_register_TCP_HMI[1071] | GVL_COM.COM_ADM100W_1.HMI_OUTPUT_L3_MAX_LOAD.Word_value[1]
1073 | 1073 | HMI | ADM100W_1 | ADM100W Internal Temperature | PLC to Client | REAL | LSW | 1 | per ADM100W config | GVL_MODBUS.Input_register_TCP_HMI[1072] | GVL_COM.COM_ADM100W_1.HMI_OUTPUT_INTERNAL_TEMPERATURE.Word_value[0]
1074 | 1074 | HMI | ADM100W_1 | ADM100W Internal Temperature | PLC to Client | REAL | MSW | 1 | per ADM100W config | GVL_MODBUS.Input_register_TCP_HMI[1073] | GVL_COM.COM_ADM100W_1.HMI_OUTPUT_INTERNAL_TEMPERATURE.Word_value[1]
1075 | 1075 | HMI | ADM100W_1 | ADM100W Active Energy | PLC to Client | REAL | LSW | 1 | per ADM100W config | GVL_MODBUS.Input_register_TCP_HMI[1074] | GVL_COM.COM_ADM100W_1.HMI_OUTPUT_ACTIVE_ENERGY.Word_value[0]
1076 | 1076 | HMI | ADM100W_1 | ADM100W Active Energy | PLC to Client | REAL | MSW | 1 | per ADM100W config | GVL_MODBUS.Input_register_TCP_HMI[1075] | GVL_COM.COM_ADM100W_1.HMI_OUTPUT_ACTIVE_ENERGY.Word_value[1]
1077 | 1077 | HMI | ADM100W_1 | ADM100W Apparent Energy | PLC to Client | REAL | LSW | 1 | per ADM100W config | GVL_MODBUS.Input_register_TCP_HMI[1076] | GVL_COM.COM_ADM100W_1.HMI_OUTPUT_APPARENT_ENERGY.Word_value[0]
1078 | 1078 | HMI | ADM100W_1 | ADM100W Apparent Energy | PLC to Client | REAL | MSW | 1 | per ADM100W config | GVL_MODBUS.Input_register_TCP_HMI[1077] | GVL_COM.COM_ADM100W_1.HMI_OUTPUT_APPARENT_ENERGY.Word_value[1]
1079 | 1079 | HMI | ADM100W_1 | ADM100W Reactive Energy | PLC to Client | REAL | LSW | 1 | per ADM100W config | GVL_MODBUS.Input_register_TCP_HMI[1078] | GVL_COM.COM_ADM100W_1.HMI_OUTPUT_REACTIVE_ENERGY.Word_value[0]
1080 | 1080 | HMI | ADM100W_1 | ADM100W Reactive Energy | PLC to Client | REAL | MSW | 1 | per ADM100W config | GVL_MODBUS.Input_register_TCP_HMI[1079] | GVL_COM.COM_ADM100W_1.HMI_OUTPUT_REACTIVE_ENERGY.Word_value[1]
1081 | 1081 | HMI | ADM100W_1 | ADM100W Total Active Power | PLC to Client | REAL | LSW | 1 | per ADM100W config | GVL_MODBUS.Input_register_TCP_HMI[1080] | GVL_COM.COM_ADM100W_1.HMI_OUTPUT_TOTAL_ACTIVE_POWER.Word_value[0]
1082 | 1082 | HMI | ADM100W_1 | ADM100W Total Active Power | PLC to Client | REAL | MSW | 1 | per ADM100W config | GVL_MODBUS.Input_register_TCP_HMI[1081] | GVL_COM.COM_ADM100W_1.HMI_OUTPUT_TOTAL_ACTIVE_POWER.Word_value[1]
1083 | 1083 | HMI | ADM100W_1 | ADM100W Total Apparent Power | PLC to Client | REAL | LSW | 1 | per ADM100W config | GVL_MODBUS.Input_register_TCP_HMI[1082] | GVL_COM.COM_ADM100W_1.HMI_OUTPUT_TOTAL_APPARENT_POWER.Word_value[0]
1084 | 1084 | HMI | ADM100W_1 | ADM100W Total Apparent Power | PLC to Client | REAL | MSW | 1 | per ADM100W config | GVL_MODBUS.Input_register_TCP_HMI[1083] | GVL_COM.COM_ADM100W_1.HMI_OUTPUT_TOTAL_APPARENT_POWER.Word_value[1]
1085 | 1085 | HMI | ADM100W_1 | ADM100W Total Reactive Power | PLC to Client | REAL | LSW | 1 | per ADM100W config | GVL_MODBUS.Input_register_TCP_HMI[1084] | GVL_COM.COM_ADM100W_1.HMI_OUTPUT_TOTAL_REACTIVE_POWER.Word_value[0]
1086 | 1086 | HMI | ADM100W_1 | ADM100W Total Reactive Power | PLC to Client | REAL | MSW | 1 | per ADM100W config | GVL_MODBUS.Input_register_TCP_HMI[1085] | GVL_COM.COM_ADM100W_1.HMI_OUTPUT_TOTAL_REACTIVE_POWER.Word_value[1]
1087 | 1087 | HMI | ADM100W_1 | ADM100W All Phase Power Factor | PLC to Client | REAL | LSW | 1 |  | GVL_MODBUS.Input_register_TCP_HMI[1086] | GVL_COM.COM_ADM100W_1.HMI_OUTPUT_ALL_PHASE_POWER_FACTOR.Word_value[0]
1088 | 1088 | HMI | ADM100W_1 | ADM100W All Phase Power Factor | PLC to Client | REAL | MSW | 1 |  | GVL_MODBUS.Input_register_TCP_HMI[1087] | GVL_COM.COM_ADM100W_1.HMI_OUTPUT_ALL_PHASE_POWER_FACTOR.Word_value[1]
1089 | 1089 | HMI | DOSENSOR_1 | DO Sensor Signal | PLC to Client | REAL | LSW | 1 |  | GVL_MODBUS.Input_register_TCP_HMI[1088] | GVL_COM.COM_DOSENSOR_1.HMI_OUTPUT_SIGNAL.Word_value[0]
1090 | 1090 | HMI | DOSENSOR_1 | DO Sensor Signal | PLC to Client | REAL | MSW | 1 |  | GVL_MODBUS.Input_register_TCP_HMI[1089] | GVL_COM.COM_DOSENSOR_1.HMI_OUTPUT_SIGNAL.Word_value[1]
1091 | 1091 | HMI | DIP1500_1 | DIP1500 Firmware Version | PLC to Client | WORD |  | 3+5+8 bits (major+minor+revision) |  | GVL_MODBUS.Input_register_TCP_HMI[1090] | GVL_COM.COM_DIP1500_1.HMI_OUTPUT_FIRMWARE_VERSION
1092 | 1092 | HMI | DIP1500_1 | DIP1500 Hardware Version | PLC to Client | WORD |  | 3+5+8 bits (major+minor+revision) |  | GVL_MODBUS.Input_register_TCP_HMI[1091] | GVL_COM.COM_DIP1500_1.HMI_OUTPUT_HARDWARE_VERSION
1093 | 1093 | HMI | DIP1500_1 | DIP1500 Temperature | PLC to Client | WORD |  | (raw - 500) / 10 | °C | GVL_MODBUS.Input_register_TCP_HMI[1092] | GVL_COM.COM_DIP1500_1.HMI_OUTPUT_TEMPERATURE
1094 | 1094 | HMI | DIP1500_1 | DIP1500 Float Level Alarm | PLC to Client | WORD |  | 1 |  | GVL_MODBUS.Input_register_TCP_HMI[1093] | GVL_COM.COM_DIP1500_1.HMI_OUTPUT_FLOAT_LEVEL_ALARM
1095 | 1095 | HMI | DIP1500_1 | DIP1500 Digital Output Value | PLC to Client | WORD |  | 1 |  | GVL_MODBUS.Input_register_TCP_HMI[1094] | GVL_COM.COM_DIP1500_1.HMI_OUTPUT_DIGITAL_OUTPUT_VALUE
1096 | 1096 | HMI | DIP1500_1 | DIP1500 Real-Time Run Time Or Volume | PLC to Client | REAL | LSW | 1 | ms (time mode) / ml (volume mode) | GVL_MODBUS.Input_register_TCP_HMI[1095] | GVL_COM.COM_DIP1500_1.HMI_OUTPUT_REAL_TIME_RUN_TIME_OR_VOLUME.Word_value[0]
1097 | 1097 | HMI | DIP1500_1 | DIP1500 Real-Time Run Time Or Volume | PLC to Client | REAL | MSW | 1 | ms (time mode) / ml (volume mode) | GVL_MODBUS.Input_register_TCP_HMI[1096] | GVL_COM.COM_DIP1500_1.HMI_OUTPUT_REAL_TIME_RUN_TIME_OR_VOLUME.Word_value[1]
1098 | 1098 | HMI | DIP1500_1 | DIP1500 Accumulated Run Time Or Volume | PLC to Client | REAL | LSW | 1 | ms (time mode) / ml (volume mode) | GVL_MODBUS.Input_register_TCP_HMI[1097] | GVL_COM.COM_DIP1500_1.HMI_OUTPUT_ACCUMULATED_RUN_TIME_OR_VOLUME.Word_value[0]
1099 | 1099 | HMI | DIP1500_1 | DIP1500 Accumulated Run Time Or Volume | PLC to Client | REAL | MSW | 1 | ms (time mode) / ml (volume mode) | GVL_MODBUS.Input_register_TCP_HMI[1098] | GVL_COM.COM_DIP1500_1.HMI_OUTPUT_ACCUMULATED_RUN_TIME_OR_VOLUME.Word_value[1]
Note on A1: Address in the PLC Modbus TCP server : coils and registers from 1, discrete inputs from 10001. GVL_MODBUS index = address - 1 (discrete inputs : address - 10001).
Note on B1: Address typed in the client. FUXA : discrete inputs 100001.., others = Modbus address.
Note on C1: Supervision or device that reads / writes the address. Each client has its own address range (sheet CLIENTS).
Note on D1: Instance that owns the value (GVL_COM.COM_<instance>).
Note on E1: Readable name of the value. Used as tag name in FUXA and as label in the supervisions.
Note on F1: Client to PLC : coils and holding registers written by the client. PLC to Client : discrete inputs and input registers read by the client.
Note on G1: Type of the value seen by the client. REAL uses 2 registers.
Note on H1: 32-bit value split in 2 registers : MSW = most significant word, LSW = least significant word. Empty for 16-bit and BOOL.
Note on I1: Conversion raw value -> engineering value, as written in the equipment manual. "1" = no conversion.
Note on J1: Engineering unit of the value (free text).
Note on K1: Element of GVL_MODBUS mapped in the CODESYS device I/O mapping (Modbus server or slave channel). GVL_MODBUS = exchange variables only.
Note on L1: Variable of GVL_COM copied to / from GVL_MODBUS by GFC_COM_IN / GFC_COM_OUT.
Note on M1: Free text. In TEMPLATE_TCP : sheet of MODBUS_TCP where the row goes.

## HOLDING_REGISTERS
Modbus address | Client address | Client | Instance | Name | Direction | Type | Word | Scale | Unit | GVL_MODBUS variable | GVL_COM variable | Comment
1 | 1 | FUXA | DIP1500_1 | DIP1500 Motor Speed | Client to PLC | REAL | LSW | 1 | rpm | GVL_MODBUS.Holding_register_TCP_HMI[0] | GVL_COM.COM_DIP1500_1.SCADA_INPUT_MOTOR_SPEED.Word_value[0]
2 | 2 | FUXA | DIP1500_1 | DIP1500 Motor Speed | Client to PLC | REAL | MSW | 1 | rpm | GVL_MODBUS.Holding_register_TCP_HMI[1] | GVL_COM.COM_DIP1500_1.SCADA_INPUT_MOTOR_SPEED.Word_value[1]
3 | 3 | FUXA | DIP1500_1 | DIP1500 Max Motor Speed | Client to PLC | REAL | LSW | 1 | rpm | GVL_MODBUS.Holding_register_TCP_HMI[2] | GVL_COM.COM_DIP1500_1.SCADA_INPUT_MAX_MOTOR_SPEED.Word_value[0]
4 | 4 | FUXA | DIP1500_1 | DIP1500 Max Motor Speed | Client to PLC | REAL | MSW | 1 | rpm | GVL_MODBUS.Holding_register_TCP_HMI[3] | GVL_COM.COM_DIP1500_1.SCADA_INPUT_MAX_MOTOR_SPEED.Word_value[1]
5 | 5 | FUXA | DIP1500_1 | DIP1500 Run Time Or Volume Setpoint | Client to PLC | REAL | LSW | 1 | ms (time mode) / ml (volume mode) | GVL_MODBUS.Holding_register_TCP_HMI[4] | GVL_COM.COM_DIP1500_1.SCADA_INPUT_RUN_TIME_OR_VOLUME_SETPOINT.Word_value[0]
6 | 6 | FUXA | DIP1500_1 | DIP1500 Run Time Or Volume Setpoint | Client to PLC | REAL | MSW | 1 | ms (time mode) / ml (volume mode) | GVL_MODBUS.Holding_register_TCP_HMI[5] | GVL_COM.COM_DIP1500_1.SCADA_INPUT_RUN_TIME_OR_VOLUME_SETPOINT.Word_value[1]
7 | 7 | FUXA | DIP1500_1 | DIP1500 Flow Rate Or Speed Calibration Coefficient | Client to PLC | REAL | LSW | 1 | ml/min or rpm | GVL_MODBUS.Holding_register_TCP_HMI[6] | GVL_COM.COM_DIP1500_1.SCADA_INPUT_FLOW_RATE_OR_SPEED_CALIBRATION_COEFFICIENT.Word_value[0]
8 | 8 | FUXA | DIP1500_1 | DIP1500 Flow Rate Or Speed Calibration Coefficient | Client to PLC | REAL | MSW | 1 | ml/min or rpm | GVL_MODBUS.Holding_register_TCP_HMI[7] | GVL_COM.COM_DIP1500_1.SCADA_INPUT_FLOW_RATE_OR_SPEED_CALIBRATION_COEFFICIENT.Word_value[1]
9 | 9 | FUXA | DIP1500_1 | DIP1500 Foot Switch Input Mode | Client to PLC | WORD |  | 1 |  | GVL_MODBUS.Holding_register_TCP_HMI[8] | GVL_COM.COM_DIP1500_1.SCADA_INPUT_FOOT_SWITCH_INPUT_MODE
10 | 10 | FUXA | DIP1500_1 | DIP1500 Liquid Level Input Mode | Client to PLC | WORD |  | 1 |  | GVL_MODBUS.Holding_register_TCP_HMI[9] | GVL_COM.COM_DIP1500_1.SCADA_INPUT_LIQUID_LEVEL_INPUT_MODE
11 | 11 | FUXA | DIP1500_1 | DIP1500 State Output Mode | Client to PLC | WORD |  | 1 |  | GVL_MODBUS.Holding_register_TCP_HMI[10] | GVL_COM.COM_DIP1500_1.SCADA_INPUT_STATE_OUTPUT_MODE
12 | 12 | FUXA | DIP1500_1 | DIP1500 Communication Address | Client to PLC | WORD |  | 1 |  | GVL_MODBUS.Holding_register_TCP_HMI[11] | GVL_COM.COM_DIP1500_1.SCADA_INPUT_COMMUNICATION_ADDRESS
13 | 13 | FUXA | DIP1500_1 | DIP1500 Baud Rate Index | Client to PLC | WORD |  | 1 | index | GVL_MODBUS.Holding_register_TCP_HMI[12] | GVL_COM.COM_DIP1500_1.SCADA_INPUT_BAUD_RATE_INDEX
1001 | 1001 | HMI | DIP1500_1 | DIP1500 Motor Speed | Client to PLC | REAL | LSW | 1 | rpm | GVL_MODBUS.Holding_register_TCP_HMI[1000] | GVL_COM.COM_DIP1500_1.HMI_INPUT_MOTOR_SPEED.Word_value[0]
1002 | 1002 | HMI | DIP1500_1 | DIP1500 Motor Speed | Client to PLC | REAL | MSW | 1 | rpm | GVL_MODBUS.Holding_register_TCP_HMI[1001] | GVL_COM.COM_DIP1500_1.HMI_INPUT_MOTOR_SPEED.Word_value[1]
1003 | 1003 | HMI | DIP1500_1 | DIP1500 Max Motor Speed | Client to PLC | REAL | LSW | 1 | rpm | GVL_MODBUS.Holding_register_TCP_HMI[1002] | GVL_COM.COM_DIP1500_1.HMI_INPUT_MAX_MOTOR_SPEED.Word_value[0]
1004 | 1004 | HMI | DIP1500_1 | DIP1500 Max Motor Speed | Client to PLC | REAL | MSW | 1 | rpm | GVL_MODBUS.Holding_register_TCP_HMI[1003] | GVL_COM.COM_DIP1500_1.HMI_INPUT_MAX_MOTOR_SPEED.Word_value[1]
1005 | 1005 | HMI | DIP1500_1 | DIP1500 Run Time Or Volume Setpoint | Client to PLC | REAL | LSW | 1 | ms (time mode) / ml (volume mode) | GVL_MODBUS.Holding_register_TCP_HMI[1004] | GVL_COM.COM_DIP1500_1.HMI_INPUT_RUN_TIME_OR_VOLUME_SETPOINT.Word_value[0]
1006 | 1006 | HMI | DIP1500_1 | DIP1500 Run Time Or Volume Setpoint | Client to PLC | REAL | MSW | 1 | ms (time mode) / ml (volume mode) | GVL_MODBUS.Holding_register_TCP_HMI[1005] | GVL_COM.COM_DIP1500_1.HMI_INPUT_RUN_TIME_OR_VOLUME_SETPOINT.Word_value[1]
1007 | 1007 | HMI | DIP1500_1 | DIP1500 Flow Rate Or Speed Calibration Coefficient | Client to PLC | REAL | LSW | 1 | ml/min or rpm | GVL_MODBUS.Holding_register_TCP_HMI[1006] | GVL_COM.COM_DIP1500_1.HMI_INPUT_FLOW_RATE_OR_SPEED_CALIBRATION_COEFFICIENT.Word_value[0]
1008 | 1008 | HMI | DIP1500_1 | DIP1500 Flow Rate Or Speed Calibration Coefficient | Client to PLC | REAL | MSW | 1 | ml/min or rpm | GVL_MODBUS.Holding_register_TCP_HMI[1007] | GVL_COM.COM_DIP1500_1.HMI_INPUT_FLOW_RATE_OR_SPEED_CALIBRATION_COEFFICIENT.Word_value[1]
1009 | 1009 | HMI | DIP1500_1 | DIP1500 Foot Switch Input Mode | Client to PLC | WORD |  | 1 |  | GVL_MODBUS.Holding_register_TCP_HMI[1008] | GVL_COM.COM_DIP1500_1.HMI_INPUT_FOOT_SWITCH_INPUT_MODE
1010 | 1010 | HMI | DIP1500_1 | DIP1500 Liquid Level Input Mode | Client to PLC | WORD |  | 1 |  | GVL_MODBUS.Holding_register_TCP_HMI[1009] | GVL_COM.COM_DIP1500_1.HMI_INPUT_LIQUID_LEVEL_INPUT_MODE
1011 | 1011 | HMI | DIP1500_1 | DIP1500 State Output Mode | Client to PLC | WORD |  | 1 |  | GVL_MODBUS.Holding_register_TCP_HMI[1010] | GVL_COM.COM_DIP1500_1.HMI_INPUT_STATE_OUTPUT_MODE
1012 | 1012 | HMI | DIP1500_1 | DIP1500 Communication Address | Client to PLC | WORD |  | 1 |  | GVL_MODBUS.Holding_register_TCP_HMI[1011] | GVL_COM.COM_DIP1500_1.HMI_INPUT_COMMUNICATION_ADDRESS
1013 | 1013 | HMI | DIP1500_1 | DIP1500 Baud Rate Index | Client to PLC | WORD |  | 1 | index | GVL_MODBUS.Holding_register_TCP_HMI[1012] | GVL_COM.COM_DIP1500_1.HMI_INPUT_BAUD_RATE_INDEX
Note on A1: Address in the PLC Modbus TCP server : coils and registers from 1, discrete inputs from 10001. GVL_MODBUS index = address - 1 (discrete inputs : address - 10001).
Note on B1: Address typed in the client. FUXA : discrete inputs 100001.., others = Modbus address.
Note on C1: Supervision or device that reads / writes the address. Each client has its own address range (sheet CLIENTS).
Note on D1: Instance that owns the value (GVL_COM.COM_<instance>).
Note on E1: Readable name of the value. Used as tag name in FUXA and as label in the supervisions.
Note on F1: Client to PLC : coils and holding registers written by the client. PLC to Client : discrete inputs and input registers read by the client.
Note on G1: Type of the value seen by the client. REAL uses 2 registers.
Note on H1: 32-bit value split in 2 registers : MSW = most significant word, LSW = least significant word. Empty for 16-bit and BOOL.
Note on I1: Conversion raw value -> engineering value, as written in the equipment manual. "1" = no conversion.
Note on J1: Engineering unit of the value (free text).
Note on K1: Element of GVL_MODBUS mapped in the CODESYS device I/O mapping (Modbus server or slave channel). GVL_MODBUS = exchange variables only.
Note on L1: Variable of GVL_COM copied to / from GVL_MODBUS by GFC_COM_IN / GFC_COM_OUT.
Note on M1: Free text. In TEMPLATE_TCP : sheet of MODBUS_TCP where the row goes.

## LISTS (hidden)
IEC_DUT | VALUE_TYPE | EXCHANGE | FUNCTION | RTU_DIR | TCP_DIR | WORD | WORD_ORDER | CHANNEL | TABLE | LINE | PLC_PORT | PLC_ROLE | BAUD | PARITY | DATA_BITS | STOP_BITS | TIMEOUT | OBJ_TYPE | INSTANCE | YESNO | COPIED_BY | SLOT | MODULE | MOD_TYPE | IO_TYPE | IOMAP_TYPE | SIGNAL | ZIPLINK | IO_STATUS | RACK_STATUS | CODESYS_DEV | CLIENT | TCP_ROLE | CLIENT_ORDER | KIND | COMM | INTERFACE | READ_CH | SECTION_TCP | FC_EXC | EXC_DIR
BOOL | BOOL | Modbus TCP FUXA Coil | FC01 Read Coils | Equipment to PLC | Client to PLC | MSW | ABCD (MSW first) | Read, cyclic | Coil | RTU_1 | RS-232/485 4-pin | Master | 1200 | None | 7 | 1 | 100 | ADM100W | ADM100W_1 | Yes | GFC_EXC_IN | 1 | P2-16AD-1 | AI | DI | BOOL | 24 VDC | ZL-CBL40-2 / ZL-RTB40-1 | Used | Installed | Module | FUXA | PLC = server | CDAB (Float32MLE) | Equipment | Modbus RTU | RS-485 | Cyclic | COILS | FC_EXC_UPI_LOCAL_FUXA_ADM100W | A -> B
BYTE | WORD | Modbus TCP FUXA DI | FC02 Read Discrete Inputs | PLC to Equipment | PLC to Client | LSW | CDAB (LSW first) | Write, cyclic | DI | RTU_2 | RS-232/485 RJ12 | Slave | 2400 | Even | 8 | 2 | 200 | DOSENSOR | DOSENSOR_1 | No | GFC_EXC_OUT | 2 | P2-16AD-2 | AO | DO | WORD | 4-20 mA | ZL-P2-CBL24-2 / ZL-RTB20-1 | Spare | Empty | Module_1 | HMI | PLC = client | CDAB, confirmed on the PV800 | Functional unit (UPI) | Modbus TCP | RS-232 | Rising edge | DISCRETE_INPUTS | FC_EXC_UPI_LOCAL_HMI_ADM100W | B -> A
WORD | INT | Modbus TCP FUXA IR | FC03 Read Holding Registers |  |  |  | BADC (byte swap) | Read, rising edge | IR | RTU_3 | TO CHECK |  | 4800 | Odd | TO CHECK | TO CHECK | 500 | DIP1500 | DIP1500_1 |  |  | 3 | P2-16DA-1 | DI | AI | DWORD | 0-20 mA |  | Reserved | Planned | Module_2 | WEBVISU |  | ABCD (Float32) |  | EtherNet/IP |  | Application | INPUT_REGISTERS | FC_EXC_UPI_LOCAL_WEBVISU_ADM100W
DWORD | UINT | Modbus TCP FUXA HR | FC04 Read Input Registers |  |  |  | DCBA (byte and word swap) | Write, rising edge of COM_OUTPUT_CMD_TRIGGER | HR |  |  |  | 9600 | TO CHECK |  |  | 1000 | UPI_LOCAL_FUXA | UPI_LOCAL_FUXA |  |  | 4 | P2-16DA-2 | DO | AO | INT | 0-10 V |  | TO CHECK | TO CHECK | Module_3 |  |  | TO CHECK |  | Wired I/O |  |  | HOLDING_REGISTERS | FC_EXC_UPI_LOCAL_FUXA_DOSENSOR
LWORD | DINT | Modbus TCP HMI Coil | FC05 Write Single Coil |  |  |  |  | Write, rising edge of COM_OUTPUT_CONFIG_TRIGGER |  |  |  |  | 19200 |  |  |  | 2000 | UPI_LOCAL_HMI | UPI_LOCAL_HMI |  |  | 5 | P2-08AD-1 | EMPTY |  | DINT | +/-10 V |  |  |  | Module_4 |  |  |  |  | None |  |  |  | FC_EXC_UPI_LOCAL_HMI_DOSENSOR
SINT | UDINT | Modbus TCP HMI DI | FC06 Write Single Register |  |  |  |  | Read, application |  |  |  |  | 38400 |  |  |  | TO CHECK | UPI_LOCAL_WEBVISU | UPI_LOCAL_WEBVISU |  |  | 6 | P2-08DA-1 |  |  | UINT | Dry contact |  |  |  | Module_5 | [8 empty] | FC_EXC_UPI_LOCAL_WEBVISU_DOSENSOR
INT | REAL | Modbus TCP HMI IR | FC15 Write Multiple Coils |  |  |  |  | Write, application |  |  |  |  | 57600 | [5 empty] | <INSTANCE> |  |  | 7 | P2-32ND3-1 |  |  | UDINT |  |  |  |  | Module_6 | [8 empty] | FC_EXC_UPI_LOCAL_FUXA_DIP1500
DINT | UDINT (time mode) / REAL (volume mode) | Modbus TCP HMI HR | FC16 Write Multiple Registers |  |  |  |  | TO CHECK |  |  |  |  | 115200 | [5 empty] | <INSTANCE_B> |  |  | 8 | P2-16ND3 |  |  | REAL |  |  |  |  | Module_7 | [8 empty] | FC_EXC_UPI_LOCAL_HMI_DIP1500
LINT |  | WebVisu (direct variable access) | FC23 Read/Write Multiple Registers | [9 empty] | TO CHECK | [8 empty] | 9 | P2-32NE3 | [7 empty] | Module_8 | [8 empty] | FC_EXC_UPI_LOCAL_WEBVISU_DIP1500
USINT |  | Modbus RTU (see RTU tables) | [19 empty] | 10 | P2-32TD1P | [7 empty] | Module_9
UINT |  | Modbus RTU write trigger (slave I/O mapping) | [19 empty] | 11 | P2-32TD2P | [7 empty] | Module_10
UDINT |  | Physical I/O (GVL_IOMAP, GFC_IO) | [20 empty] | P2-16TD2P
ULINT |  | Exchange (GFC_EXC) | [20 empty] | P2-08TRS
REAL |  | Persistent parameter (GVL_PA) | [20 empty] | P2-FILL
LREAL
TIME
STRING
DUT_Union_Real_Word
TON
TOF
TP
R_TRIG
F_TRIG
ARRAY[0..1] OF WORD
ARRAY[0..7] OF BOOL