## README
Object type : ADM100W
One file per object type. Everything here is the same for every instance of the type.
Instance data (name, addresses, slave address, parameter values, exchanges) is in the project files :
IO_PHYSICAL, MODBUS_TCP, MODBUS_RTU, PARAMETERS_PA, EXCHANGES_EXC
Sheets:
TYPE : identity of the type (FB, DUT names, kind, communication)
DUT_COM : communication data. Prefixes COM_ (Modbus RTU), SCADA_ (FUXA), HMI_ (local HMI), WEBVISU_ (WebVisu)
DUT_EXC : exchanges with other instances (EXC_) and functional units (UPI_)
DUT_INT : internal variables of the FB (INTERN)
DUT_IO : wired PLC I/O
DUT_PA : parameters. "Default value" = declaration value of the DUT
RTU_DEFAULT : Modbus RTU properties of the equipment (empty if not on Modbus RTU)
RTU_COILS, RTU_DI, RTU_IR, RTU_HR : Modbus RTU register map of the equipment
Rules:
One row per DUT member, in declaration order. "Section" starts a new comment block in the DUT.
Default value : empty = type default (FALSE, 0).
RTU tables : one row per address. A 32-bit value uses 2 rows (Word = MSW / LSW).
An empty sheet keeps its header row.
Cells marked "TO CHECK" (yellow) are values not confirmed yet.
Instance templates (copy into the project files, then replace <INSTANCE> by the instance name):
TEMPLATE_PA -> new sheet <instance> of PARAMETERS_PA
TEMPLATE_RTU -> new sheet <instance> of MODBUS_RTU (+ one row in SLAVES)
TEMPLATE_EXC -> rows of EXCHANGES_EXC / CALLS (GFC_EXC calls)
TEMPLATE_TCP -> rows of MODBUS_TCP, in the sheet named in "Comment", with free addresses of the client range
TEMPLATE_IO -> rows of IO_PHYSICAL / IO, on free channels
<INSTANCE>, <SOURCE>, <DESTINATION> are placeholders recognized by the generator.

## TYPE
Key | Value | Comment
Object type | ADM100W | Suffix of the DUT names
Kind | Equipment | Equipment or Functional unit (UPI)
Description | Trumeter ADM100W power meter
Function block | FB_INST_ADM100W
Project folder | 01-FB_ADM100W | Folder under Function Blocs / FB
Communication | Modbus RTU | Modbus RTU, Wired I/O, None
DUT_COM | DUT_COM_ADM100W
DUT_EXC | DUT_EXC_ADM100W
DUT_INT | DUT_INT_ADM100W
DUT_IO | DUT_IO_ADM100W
DUT_PA | DUT_PA_ADM100W
Note on A1: Name of the setting. Do not change it, the generator reads the value by this key.
Note on B1: Value of the setting. Use the drop-down list when there is one.
Note on C1: Free text. Not used by the generator.

## DUT_COM
Section | Member | Type | Default value | Unit | Comment | Exchange
COM : Modbus RTU, input (equipment to PLC) | COM_INPUT_IR | ARRAY[0..87] OF WORD |  |  | Input registers 0..87, 32-bit float, MSW first (ABCD) | Modbus RTU (see RTU tables)
| COM_INPUT_COILS | ARRAY[0..1] OF BYTE |  |  | Coils 0..9 = alarms 1..10 (byte.bit) | Modbus RTU (see RTU tables)
SCADA (FUXA) : input (to PLC) | SCADA_INPUT_LOCAL_REQUEST | BOOL |  |  | Coil 12 ¦ ADM100W Local Request | Modbus TCP FUXA Coil
| SCADA_INPUT_AUTO_REQUEST | BOOL |  |  | Coil 13 ¦ ADM100W Auto Request | Modbus TCP FUXA Coil
SCADA (FUXA) : output (from PLC) | SCADA_OUTPUT_ALARM_1_STATUS | BOOL |  |  | DI 10003 ¦ ADM100W Alarm 1 Status | Modbus TCP FUXA DI
| SCADA_OUTPUT_ALARM_2_STATUS | BOOL |  |  | DI 10004 ¦ ADM100W Alarm 2 Status | Modbus TCP FUXA DI
| SCADA_OUTPUT_ALARM_3_STATUS | BOOL |  |  | DI 10005 ¦ ADM100W Alarm 3 Status | Modbus TCP FUXA DI
| SCADA_OUTPUT_ALARM_4_STATUS | BOOL |  |  | DI 10006 ¦ ADM100W Alarm 4 Status | Modbus TCP FUXA DI
| SCADA_OUTPUT_ALARM_5_STATUS | BOOL |  |  | DI 10007 ¦ ADM100W Alarm 5 Status | Modbus TCP FUXA DI
| SCADA_OUTPUT_ALARM_6_STATUS | BOOL |  |  | DI 10008 ¦ ADM100W Alarm 6 Status | Modbus TCP FUXA DI
| SCADA_OUTPUT_ALARM_7_STATUS | BOOL |  |  | DI 10009 ¦ ADM100W Alarm 7 Status | Modbus TCP FUXA DI
| SCADA_OUTPUT_ALARM_8_STATUS | BOOL |  |  | DI 10010 ¦ ADM100W Alarm 8 Status | Modbus TCP FUXA DI
| SCADA_OUTPUT_ALARM_9_STATUS | BOOL |  |  | DI 10011 ¦ ADM100W Alarm 9 Status | Modbus TCP FUXA DI
| SCADA_OUTPUT_ALARM_10_STATUS | BOOL |  |  | DI 10012 ¦ ADM100W Alarm 10 Status | Modbus TCP FUXA DI
| SCADA_OUTPUT_LOCAL_FUXA_ACTIVE | BOOL |  |  | DI 10017 ¦ ADM100W Local FUXA Active | Modbus TCP FUXA DI
| SCADA_OUTPUT_LOCAL_HMI_ACTIVE | BOOL |  |  | DI 10018 ¦ ADM100W Local HMI Active | Modbus TCP FUXA DI
| SCADA_OUTPUT_FREQUENCY | DUT_Union_Real_Word |  | Hz | IR 1-2 ¦ ADM100W Frequency ¦ Hz | Modbus TCP FUXA IR
| SCADA_OUTPUT_L1_L2_VOLTAGE | DUT_Union_Real_Word |  | V | IR 3-4 ¦ ADM100W L1-L2 Voltage ¦ V | Modbus TCP FUXA IR
| SCADA_OUTPUT_L1_N_VOLTAGE | DUT_Union_Real_Word |  | V | IR 5-6 ¦ ADM100W L1-N Voltage ¦ V | Modbus TCP FUXA IR
| SCADA_OUTPUT_L1_CURRENT | DUT_Union_Real_Word |  | A | IR 7-8 ¦ ADM100W L1 Current ¦ A | Modbus TCP FUXA IR
| SCADA_OUTPUT_L1_ACTIVE_POWER | DUT_Union_Real_Word |  |  | IR 9-10 ¦ ADM100W L1 Active Power | Modbus TCP FUXA IR
| SCADA_OUTPUT_L1_APPARENT_POWER | DUT_Union_Real_Word |  |  | IR 11-12 ¦ ADM100W L1 Apparent Power | Modbus TCP FUXA IR
| SCADA_OUTPUT_L1_REACTIVE_POWER | DUT_Union_Real_Word |  |  | IR 13-14 ¦ ADM100W L1 Reactive Power | Modbus TCP FUXA IR
| SCADA_OUTPUT_L1_CURRENT_PHASE_ANGLE | DUT_Union_Real_Word |  | ° | IR 15-16 ¦ ADM100W L1 Current Phase Angle ¦ deg | Modbus TCP FUXA IR
| SCADA_OUTPUT_L1_POWER_FACTOR | DUT_Union_Real_Word |  |  | IR 17-18 ¦ ADM100W L1 Power Factor | Modbus TCP FUXA IR
| SCADA_OUTPUT_L1_VOLTAGE_THD | DUT_Union_Real_Word |  | % | IR 19-20 ¦ ADM100W L1 Voltage THD ¦ % | Modbus TCP FUXA IR
| SCADA_OUTPUT_L1_CURRENT_THD | DUT_Union_Real_Word |  | % | IR 21-22 ¦ ADM100W L1 Current THD ¦ % | Modbus TCP FUXA IR
| SCADA_OUTPUT_L1_MAX_LOAD | DUT_Union_Real_Word |  |  | IR 23-24 ¦ ADM100W L1 Max Load | Modbus TCP FUXA IR
| SCADA_OUTPUT_L1_L2_VOLTAGE_PHASE_ANGLE | DUT_Union_Real_Word |  | ° | IR 25-26 ¦ ADM100W L1-L2 Voltage Phase Angle ¦ deg | Modbus TCP FUXA IR
| SCADA_OUTPUT_L2_L3_VOLTAGE | DUT_Union_Real_Word |  | V | IR 27-28 ¦ ADM100W L2-L3 Voltage ¦ V | Modbus TCP FUXA IR
| SCADA_OUTPUT_L2_N_VOLTAGE | DUT_Union_Real_Word |  | V | IR 29-30 ¦ ADM100W L2-N Voltage ¦ V | Modbus TCP FUXA IR
| SCADA_OUTPUT_L2_CURRENT | DUT_Union_Real_Word |  | A | IR 31-32 ¦ ADM100W L2 Current ¦ A | Modbus TCP FUXA IR
| SCADA_OUTPUT_L2_ACTIVE_POWER | DUT_Union_Real_Word |  |  | IR 33-34 ¦ ADM100W L2 Active Power | Modbus TCP FUXA IR
| SCADA_OUTPUT_L2_APPARENT_POWER | DUT_Union_Real_Word |  |  | IR 35-36 ¦ ADM100W L2 Apparent Power | Modbus TCP FUXA IR
| SCADA_OUTPUT_L2_REACTIVE_POWER | DUT_Union_Real_Word |  |  | IR 37-38 ¦ ADM100W L2 Reactive Power | Modbus TCP FUXA IR
| SCADA_OUTPUT_L2_CURRENT_PHASE_ANGLE | DUT_Union_Real_Word |  | ° | IR 39-40 ¦ ADM100W L2 Current Phase Angle ¦ deg | Modbus TCP FUXA IR
| SCADA_OUTPUT_L2_POWER_FACTOR | DUT_Union_Real_Word |  |  | IR 41-42 ¦ ADM100W L2 Power Factor | Modbus TCP FUXA IR
| SCADA_OUTPUT_L2_VOLTAGE_THD | DUT_Union_Real_Word |  | % | IR 43-44 ¦ ADM100W L2 Voltage THD ¦ % | Modbus TCP FUXA IR
| SCADA_OUTPUT_L2_CURRENT_THD | DUT_Union_Real_Word |  | % | IR 45-46 ¦ ADM100W L2 Current THD ¦ % | Modbus TCP FUXA IR
| SCADA_OUTPUT_L2_MAX_LOAD | DUT_Union_Real_Word |  |  | IR 47-48 ¦ ADM100W L2 Max Load | Modbus TCP FUXA IR
| SCADA_OUTPUT_L1_L3_VOLTAGE_PHASE_ANGLE | DUT_Union_Real_Word |  | ° | IR 49-50 ¦ ADM100W L1-L3 Voltage Phase Angle ¦ deg | Modbus TCP FUXA IR
| SCADA_OUTPUT_L3_L1_VOLTAGE | DUT_Union_Real_Word |  | V | IR 51-52 ¦ ADM100W L3-L1 Voltage ¦ V | Modbus TCP FUXA IR
| SCADA_OUTPUT_L3_N_VOLTAGE | DUT_Union_Real_Word |  | V | IR 53-54 ¦ ADM100W L3-N Voltage ¦ V | Modbus TCP FUXA IR
| SCADA_OUTPUT_L3_CURRENT | DUT_Union_Real_Word |  | A | IR 55-56 ¦ ADM100W L3 Current ¦ A | Modbus TCP FUXA IR
| SCADA_OUTPUT_L3_ACTIVE_POWER | DUT_Union_Real_Word |  |  | IR 57-58 ¦ ADM100W L3 Active Power | Modbus TCP FUXA IR
| SCADA_OUTPUT_L3_APPARENT_POWER | DUT_Union_Real_Word |  |  | IR 59-60 ¦ ADM100W L3 Apparent Power | Modbus TCP FUXA IR
| SCADA_OUTPUT_L3_REACTIVE_POWER | DUT_Union_Real_Word |  |  | IR 61-62 ¦ ADM100W L3 Reactive Power | Modbus TCP FUXA IR
| SCADA_OUTPUT_L3_CURRENT_PHASE_ANGLE | DUT_Union_Real_Word |  | ° | IR 63-64 ¦ ADM100W L3 Current Phase Angle ¦ deg | Modbus TCP FUXA IR
| SCADA_OUTPUT_L3_POWER_FACTOR | DUT_Union_Real_Word |  |  | IR 65-66 ¦ ADM100W L3 Power Factor | Modbus TCP FUXA IR
| SCADA_OUTPUT_L3_VOLTAGE_THD | DUT_Union_Real_Word |  | % | IR 67-68 ¦ ADM100W L3 Voltage THD ¦ % | Modbus TCP FUXA IR
| SCADA_OUTPUT_L3_CURRENT_THD | DUT_Union_Real_Word |  | % | IR 69-70 ¦ ADM100W L3 Current THD ¦ % | Modbus TCP FUXA IR
| SCADA_OUTPUT_L3_MAX_LOAD | DUT_Union_Real_Word |  |  | IR 71-72 ¦ ADM100W L3 Max Load | Modbus TCP FUXA IR
| SCADA_OUTPUT_INTERNAL_TEMPERATURE | DUT_Union_Real_Word |  |  | IR 73-74 ¦ ADM100W Internal Temperature | Modbus TCP FUXA IR
| SCADA_OUTPUT_ACTIVE_ENERGY | DUT_Union_Real_Word |  |  | IR 75-76 ¦ ADM100W Active Energy | Modbus TCP FUXA IR
| SCADA_OUTPUT_APPARENT_ENERGY | DUT_Union_Real_Word |  |  | IR 77-78 ¦ ADM100W Apparent Energy | Modbus TCP FUXA IR
| SCADA_OUTPUT_REACTIVE_ENERGY | DUT_Union_Real_Word |  |  | IR 79-80 ¦ ADM100W Reactive Energy | Modbus TCP FUXA IR
| SCADA_OUTPUT_TOTAL_ACTIVE_POWER | DUT_Union_Real_Word |  |  | IR 81-82 ¦ ADM100W Total Active Power | Modbus TCP FUXA IR
| SCADA_OUTPUT_TOTAL_APPARENT_POWER | DUT_Union_Real_Word |  |  | IR 83-84 ¦ ADM100W Total Apparent Power | Modbus TCP FUXA IR
| SCADA_OUTPUT_TOTAL_REACTIVE_POWER | DUT_Union_Real_Word |  |  | IR 85-86 ¦ ADM100W Total Reactive Power | Modbus TCP FUXA IR
| SCADA_OUTPUT_ALL_PHASE_POWER_FACTOR | DUT_Union_Real_Word |  |  | IR 87-88 ¦ ADM100W All Phase Power Factor | Modbus TCP FUXA IR
HMI (local panel, FUXA address + 1000) : input (to PLC) | HMI_INPUT_LOCAL_REQUEST | BOOL |  |  | Coil 1012 ¦ ADM100W Local Request | Modbus TCP HMI Coil
| HMI_INPUT_AUTO_REQUEST | BOOL |  |  | Coil 1013 ¦ ADM100W Auto Request | Modbus TCP HMI Coil
HMI (local panel, FUXA address + 1000) : output (from PLC) | HMI_OUTPUT_ALARM_1_STATUS | BOOL |  |  | DI 11003 ¦ ADM100W Alarm 1 Status | Modbus TCP HMI DI
| HMI_OUTPUT_ALARM_2_STATUS | BOOL |  |  | DI 11004 ¦ ADM100W Alarm 2 Status | Modbus TCP HMI DI
| HMI_OUTPUT_ALARM_3_STATUS | BOOL |  |  | DI 11005 ¦ ADM100W Alarm 3 Status | Modbus TCP HMI DI
| HMI_OUTPUT_ALARM_4_STATUS | BOOL |  |  | DI 11006 ¦ ADM100W Alarm 4 Status | Modbus TCP HMI DI
| HMI_OUTPUT_ALARM_5_STATUS | BOOL |  |  | DI 11007 ¦ ADM100W Alarm 5 Status | Modbus TCP HMI DI
| HMI_OUTPUT_ALARM_6_STATUS | BOOL |  |  | DI 11008 ¦ ADM100W Alarm 6 Status | Modbus TCP HMI DI
| HMI_OUTPUT_ALARM_7_STATUS | BOOL |  |  | DI 11009 ¦ ADM100W Alarm 7 Status | Modbus TCP HMI DI
| HMI_OUTPUT_ALARM_8_STATUS | BOOL |  |  | DI 11010 ¦ ADM100W Alarm 8 Status | Modbus TCP HMI DI
| HMI_OUTPUT_ALARM_9_STATUS | BOOL |  |  | DI 11011 ¦ ADM100W Alarm 9 Status | Modbus TCP HMI DI
| HMI_OUTPUT_ALARM_10_STATUS | BOOL |  |  | DI 11012 ¦ ADM100W Alarm 10 Status | Modbus TCP HMI DI
| HMI_OUTPUT_LOCAL_ACTIVE | BOOL |  |  | DI 11018 ¦ ADM100W Local Active | Modbus TCP HMI DI
| HMI_OUTPUT_FREQUENCY | DUT_Union_Real_Word |  | Hz | IR 1001-1002 ¦ ADM100W Frequency ¦ Hz | Modbus TCP HMI IR
| HMI_OUTPUT_L1_L2_VOLTAGE | DUT_Union_Real_Word |  | V | IR 1003-1004 ¦ ADM100W L1-L2 Voltage ¦ V | Modbus TCP HMI IR
| HMI_OUTPUT_L1_N_VOLTAGE | DUT_Union_Real_Word |  | V | IR 1005-1006 ¦ ADM100W L1-N Voltage ¦ V | Modbus TCP HMI IR
| HMI_OUTPUT_L1_CURRENT | DUT_Union_Real_Word |  | A | IR 1007-1008 ¦ ADM100W L1 Current ¦ A | Modbus TCP HMI IR
| HMI_OUTPUT_L1_ACTIVE_POWER | DUT_Union_Real_Word |  |  | IR 1009-1010 ¦ ADM100W L1 Active Power | Modbus TCP HMI IR
| HMI_OUTPUT_L1_APPARENT_POWER | DUT_Union_Real_Word |  |  | IR 1011-1012 ¦ ADM100W L1 Apparent Power | Modbus TCP HMI IR
| HMI_OUTPUT_L1_REACTIVE_POWER | DUT_Union_Real_Word |  |  | IR 1013-1014 ¦ ADM100W L1 Reactive Power | Modbus TCP HMI IR
| HMI_OUTPUT_L1_CURRENT_PHASE_ANGLE | DUT_Union_Real_Word |  | ° | IR 1015-1016 ¦ ADM100W L1 Current Phase Angle ¦ deg | Modbus TCP HMI IR
| HMI_OUTPUT_L1_POWER_FACTOR | DUT_Union_Real_Word |  |  | IR 1017-1018 ¦ ADM100W L1 Power Factor | Modbus TCP HMI IR
| HMI_OUTPUT_L1_VOLTAGE_THD | DUT_Union_Real_Word |  | % | IR 1019-1020 ¦ ADM100W L1 Voltage THD ¦ % | Modbus TCP HMI IR
| HMI_OUTPUT_L1_CURRENT_THD | DUT_Union_Real_Word |  | % | IR 1021-1022 ¦ ADM100W L1 Current THD ¦ % | Modbus TCP HMI IR
| HMI_OUTPUT_L1_MAX_LOAD | DUT_Union_Real_Word |  |  | IR 1023-1024 ¦ ADM100W L1 Max Load | Modbus TCP HMI IR
| HMI_OUTPUT_L1_L2_VOLTAGE_PHASE_ANGLE | DUT_Union_Real_Word |  | ° | IR 1025-1026 ¦ ADM100W L1-L2 Voltage Phase Angle ¦ deg | Modbus TCP HMI IR
| HMI_OUTPUT_L2_L3_VOLTAGE | DUT_Union_Real_Word |  | V | IR 1027-1028 ¦ ADM100W L2-L3 Voltage ¦ V | Modbus TCP HMI IR
| HMI_OUTPUT_L2_N_VOLTAGE | DUT_Union_Real_Word |  | V | IR 1029-1030 ¦ ADM100W L2-N Voltage ¦ V | Modbus TCP HMI IR
| HMI_OUTPUT_L2_CURRENT | DUT_Union_Real_Word |  | A | IR 1031-1032 ¦ ADM100W L2 Current ¦ A | Modbus TCP HMI IR
| HMI_OUTPUT_L2_ACTIVE_POWER | DUT_Union_Real_Word |  |  | IR 1033-1034 ¦ ADM100W L2 Active Power | Modbus TCP HMI IR
| HMI_OUTPUT_L2_APPARENT_POWER | DUT_Union_Real_Word |  |  | IR 1035-1036 ¦ ADM100W L2 Apparent Power | Modbus TCP HMI IR
| HMI_OUTPUT_L2_REACTIVE_POWER | DUT_Union_Real_Word |  |  | IR 1037-1038 ¦ ADM100W L2 Reactive Power | Modbus TCP HMI IR
| HMI_OUTPUT_L2_CURRENT_PHASE_ANGLE | DUT_Union_Real_Word |  | ° | IR 1039-1040 ¦ ADM100W L2 Current Phase Angle ¦ deg | Modbus TCP HMI IR
| HMI_OUTPUT_L2_POWER_FACTOR | DUT_Union_Real_Word |  |  | IR 1041-1042 ¦ ADM100W L2 Power Factor | Modbus TCP HMI IR
| HMI_OUTPUT_L2_VOLTAGE_THD | DUT_Union_Real_Word |  | % | IR 1043-1044 ¦ ADM100W L2 Voltage THD ¦ % | Modbus TCP HMI IR
| HMI_OUTPUT_L2_CURRENT_THD | DUT_Union_Real_Word |  | % | IR 1045-1046 ¦ ADM100W L2 Current THD ¦ % | Modbus TCP HMI IR
| HMI_OUTPUT_L2_MAX_LOAD | DUT_Union_Real_Word |  |  | IR 1047-1048 ¦ ADM100W L2 Max Load | Modbus TCP HMI IR
| HMI_OUTPUT_L1_L3_VOLTAGE_PHASE_ANGLE | DUT_Union_Real_Word |  | ° | IR 1049-1050 ¦ ADM100W L1-L3 Voltage Phase Angle ¦ deg | Modbus TCP HMI IR
| HMI_OUTPUT_L3_L1_VOLTAGE | DUT_Union_Real_Word |  | V | IR 1051-1052 ¦ ADM100W L3-L1 Voltage ¦ V | Modbus TCP HMI IR
| HMI_OUTPUT_L3_N_VOLTAGE | DUT_Union_Real_Word |  | V | IR 1053-1054 ¦ ADM100W L3-N Voltage ¦ V | Modbus TCP HMI IR
| HMI_OUTPUT_L3_CURRENT | DUT_Union_Real_Word |  | A | IR 1055-1056 ¦ ADM100W L3 Current ¦ A | Modbus TCP HMI IR
| HMI_OUTPUT_L3_ACTIVE_POWER | DUT_Union_Real_Word |  |  | IR 1057-1058 ¦ ADM100W L3 Active Power | Modbus TCP HMI IR
| HMI_OUTPUT_L3_APPARENT_POWER | DUT_Union_Real_Word |  |  | IR 1059-1060 ¦ ADM100W L3 Apparent Power | Modbus TCP HMI IR
| HMI_OUTPUT_L3_REACTIVE_POWER | DUT_Union_Real_Word |  |  | IR 1061-1062 ¦ ADM100W L3 Reactive Power | Modbus TCP HMI IR
| HMI_OUTPUT_L3_CURRENT_PHASE_ANGLE | DUT_Union_Real_Word |  | ° | IR 1063-1064 ¦ ADM100W L3 Current Phase Angle ¦ deg | Modbus TCP HMI IR
| HMI_OUTPUT_L3_POWER_FACTOR | DUT_Union_Real_Word |  |  | IR 1065-1066 ¦ ADM100W L3 Power Factor | Modbus TCP HMI IR
| HMI_OUTPUT_L3_VOLTAGE_THD | DUT_Union_Real_Word |  | % | IR 1067-1068 ¦ ADM100W L3 Voltage THD ¦ % | Modbus TCP HMI IR
| HMI_OUTPUT_L3_CURRENT_THD | DUT_Union_Real_Word |  | % | IR 1069-1070 ¦ ADM100W L3 Current THD ¦ % | Modbus TCP HMI IR
| HMI_OUTPUT_L3_MAX_LOAD | DUT_Union_Real_Word |  |  | IR 1071-1072 ¦ ADM100W L3 Max Load | Modbus TCP HMI IR
| HMI_OUTPUT_INTERNAL_TEMPERATURE | DUT_Union_Real_Word |  |  | IR 1073-1074 ¦ ADM100W Internal Temperature | Modbus TCP HMI IR
| HMI_OUTPUT_ACTIVE_ENERGY | DUT_Union_Real_Word |  |  | IR 1075-1076 ¦ ADM100W Active Energy | Modbus TCP HMI IR
| HMI_OUTPUT_APPARENT_ENERGY | DUT_Union_Real_Word |  |  | IR 1077-1078 ¦ ADM100W Apparent Energy | Modbus TCP HMI IR
| HMI_OUTPUT_REACTIVE_ENERGY | DUT_Union_Real_Word |  |  | IR 1079-1080 ¦ ADM100W Reactive Energy | Modbus TCP HMI IR
| HMI_OUTPUT_TOTAL_ACTIVE_POWER | DUT_Union_Real_Word |  |  | IR 1081-1082 ¦ ADM100W Total Active Power | Modbus TCP HMI IR
| HMI_OUTPUT_TOTAL_APPARENT_POWER | DUT_Union_Real_Word |  |  | IR 1083-1084 ¦ ADM100W Total Apparent Power | Modbus TCP HMI IR
| HMI_OUTPUT_TOTAL_REACTIVE_POWER | DUT_Union_Real_Word |  |  | IR 1085-1086 ¦ ADM100W Total Reactive Power | Modbus TCP HMI IR
| HMI_OUTPUT_ALL_PHASE_POWER_FACTOR | DUT_Union_Real_Word |  |  | IR 1087-1088 ¦ ADM100W All Phase Power Factor | Modbus TCP HMI IR
WEBVISU : direct IEC variable | WEBVISU_INPUT_LOCAL_REQUEST | BOOL |  |  | ADM100W Local Request | WebVisu (direct variable access)
| WEBVISU_INPUT_AUTO_REQUEST | BOOL |  |  | ADM100W Auto Request | WebVisu (direct variable access)
| WEBVISU_OUTPUT_ALARM_1_STATUS | BOOL |  |  | ADM100W Alarm 1 Status | WebVisu (direct variable access)
| WEBVISU_OUTPUT_ALARM_2_STATUS | BOOL |  |  | ADM100W Alarm 2 Status | WebVisu (direct variable access)
| WEBVISU_OUTPUT_ALARM_3_STATUS | BOOL |  |  | ADM100W Alarm 3 Status | WebVisu (direct variable access)
| WEBVISU_OUTPUT_ALARM_4_STATUS | BOOL |  |  | ADM100W Alarm 4 Status | WebVisu (direct variable access)
| WEBVISU_OUTPUT_ALARM_5_STATUS | BOOL |  |  | ADM100W Alarm 5 Status | WebVisu (direct variable access)
| WEBVISU_OUTPUT_ALARM_6_STATUS | BOOL |  |  | ADM100W Alarm 6 Status | WebVisu (direct variable access)
| WEBVISU_OUTPUT_ALARM_7_STATUS | BOOL |  |  | ADM100W Alarm 7 Status | WebVisu (direct variable access)
| WEBVISU_OUTPUT_ALARM_8_STATUS | BOOL |  |  | ADM100W Alarm 8 Status | WebVisu (direct variable access)
| WEBVISU_OUTPUT_ALARM_9_STATUS | BOOL |  |  | ADM100W Alarm 9 Status | WebVisu (direct variable access)
| WEBVISU_OUTPUT_ALARM_10_STATUS | BOOL |  |  | ADM100W Alarm 10 Status | WebVisu (direct variable access)
| WEBVISU_OUTPUT_LOCAL_ACTIVE | BOOL |  |  | ADM100W Local Active | WebVisu (direct variable access)
| WEBVISU_OUTPUT_FREQUENCY | DUT_Union_Real_Word |  |  | ADM100W Frequency ¦ Hz | WebVisu (direct variable access)
| WEBVISU_OUTPUT_L1_L2_VOLTAGE | DUT_Union_Real_Word |  |  | ADM100W L1-L2 Voltage ¦ V | WebVisu (direct variable access)
| WEBVISU_OUTPUT_L1_N_VOLTAGE | DUT_Union_Real_Word |  |  | ADM100W L1-N Voltage ¦ V | WebVisu (direct variable access)
| WEBVISU_OUTPUT_L1_CURRENT | DUT_Union_Real_Word |  |  | ADM100W L1 Current ¦ A | WebVisu (direct variable access)
| WEBVISU_OUTPUT_L1_ACTIVE_POWER | DUT_Union_Real_Word |  |  | ADM100W L1 Active Power | WebVisu (direct variable access)
| WEBVISU_OUTPUT_L1_APPARENT_POWER | DUT_Union_Real_Word |  |  | ADM100W L1 Apparent Power | WebVisu (direct variable access)
| WEBVISU_OUTPUT_L1_REACTIVE_POWER | DUT_Union_Real_Word |  |  | ADM100W L1 Reactive Power | WebVisu (direct variable access)
| WEBVISU_OUTPUT_L1_CURRENT_PHASE_ANGLE | DUT_Union_Real_Word |  |  | ADM100W L1 Current Phase Angle ¦ deg | WebVisu (direct variable access)
| WEBVISU_OUTPUT_L1_POWER_FACTOR | DUT_Union_Real_Word |  |  | ADM100W L1 Power Factor | WebVisu (direct variable access)
| WEBVISU_OUTPUT_L1_VOLTAGE_THD | DUT_Union_Real_Word |  |  | ADM100W L1 Voltage THD ¦ % | WebVisu (direct variable access)
| WEBVISU_OUTPUT_L1_CURRENT_THD | DUT_Union_Real_Word |  |  | ADM100W L1 Current THD ¦ % | WebVisu (direct variable access)
| WEBVISU_OUTPUT_L1_MAX_LOAD | DUT_Union_Real_Word |  |  | ADM100W L1 Max Load | WebVisu (direct variable access)
| WEBVISU_OUTPUT_L1_L2_VOLTAGE_PHASE_ANGLE | DUT_Union_Real_Word |  |  | ADM100W L1-L2 Voltage Phase Angle ¦ deg | WebVisu (direct variable access)
| WEBVISU_OUTPUT_L2_L3_VOLTAGE | DUT_Union_Real_Word |  |  | ADM100W L2-L3 Voltage ¦ V | WebVisu (direct variable access)
| WEBVISU_OUTPUT_L2_N_VOLTAGE | DUT_Union_Real_Word |  |  | ADM100W L2-N Voltage ¦ V | WebVisu (direct variable access)
| WEBVISU_OUTPUT_L2_CURRENT | DUT_Union_Real_Word |  |  | ADM100W L2 Current ¦ A | WebVisu (direct variable access)
| WEBVISU_OUTPUT_L2_ACTIVE_POWER | DUT_Union_Real_Word |  |  | ADM100W L2 Active Power | WebVisu (direct variable access)
| WEBVISU_OUTPUT_L2_APPARENT_POWER | DUT_Union_Real_Word |  |  | ADM100W L2 Apparent Power | WebVisu (direct variable access)
| WEBVISU_OUTPUT_L2_REACTIVE_POWER | DUT_Union_Real_Word |  |  | ADM100W L2 Reactive Power | WebVisu (direct variable access)
| WEBVISU_OUTPUT_L2_CURRENT_PHASE_ANGLE | DUT_Union_Real_Word |  |  | ADM100W L2 Current Phase Angle ¦ deg | WebVisu (direct variable access)
| WEBVISU_OUTPUT_L2_POWER_FACTOR | DUT_Union_Real_Word |  |  | ADM100W L2 Power Factor | WebVisu (direct variable access)
| WEBVISU_OUTPUT_L2_VOLTAGE_THD | DUT_Union_Real_Word |  |  | ADM100W L2 Voltage THD ¦ % | WebVisu (direct variable access)
| WEBVISU_OUTPUT_L2_CURRENT_THD | DUT_Union_Real_Word |  |  | ADM100W L2 Current THD ¦ % | WebVisu (direct variable access)
| WEBVISU_OUTPUT_L2_MAX_LOAD | DUT_Union_Real_Word |  |  | ADM100W L2 Max Load | WebVisu (direct variable access)
| WEBVISU_OUTPUT_L1_L3_VOLTAGE_PHASE_ANGLE | DUT_Union_Real_Word |  |  | ADM100W L1-L3 Voltage Phase Angle ¦ deg | WebVisu (direct variable access)
| WEBVISU_OUTPUT_L3_L1_VOLTAGE | DUT_Union_Real_Word |  |  | ADM100W L3-L1 Voltage ¦ V | WebVisu (direct variable access)
| WEBVISU_OUTPUT_L3_N_VOLTAGE | DUT_Union_Real_Word |  |  | ADM100W L3-N Voltage ¦ V | WebVisu (direct variable access)
| WEBVISU_OUTPUT_L3_CURRENT | DUT_Union_Real_Word |  |  | ADM100W L3 Current ¦ A | WebVisu (direct variable access)
| WEBVISU_OUTPUT_L3_ACTIVE_POWER | DUT_Union_Real_Word |  |  | ADM100W L3 Active Power | WebVisu (direct variable access)
| WEBVISU_OUTPUT_L3_APPARENT_POWER | DUT_Union_Real_Word |  |  | ADM100W L3 Apparent Power | WebVisu (direct variable access)
| WEBVISU_OUTPUT_L3_REACTIVE_POWER | DUT_Union_Real_Word |  |  | ADM100W L3 Reactive Power | WebVisu (direct variable access)
| WEBVISU_OUTPUT_L3_CURRENT_PHASE_ANGLE | DUT_Union_Real_Word |  |  | ADM100W L3 Current Phase Angle ¦ deg | WebVisu (direct variable access)
| WEBVISU_OUTPUT_L3_POWER_FACTOR | DUT_Union_Real_Word |  |  | ADM100W L3 Power Factor | WebVisu (direct variable access)
| WEBVISU_OUTPUT_L3_VOLTAGE_THD | DUT_Union_Real_Word |  |  | ADM100W L3 Voltage THD ¦ % | WebVisu (direct variable access)
| WEBVISU_OUTPUT_L3_CURRENT_THD | DUT_Union_Real_Word |  |  | ADM100W L3 Current THD ¦ % | WebVisu (direct variable access)
| WEBVISU_OUTPUT_L3_MAX_LOAD | DUT_Union_Real_Word |  |  | ADM100W L3 Max Load | WebVisu (direct variable access)
| WEBVISU_OUTPUT_INTERNAL_TEMPERATURE | DUT_Union_Real_Word |  |  | ADM100W Internal Temperature | WebVisu (direct variable access)
| WEBVISU_OUTPUT_ACTIVE_ENERGY | DUT_Union_Real_Word |  |  | ADM100W Active Energy | WebVisu (direct variable access)
| WEBVISU_OUTPUT_APPARENT_ENERGY | DUT_Union_Real_Word |  |  | ADM100W Apparent Energy | WebVisu (direct variable access)
| WEBVISU_OUTPUT_REACTIVE_ENERGY | DUT_Union_Real_Word |  |  | ADM100W Reactive Energy | WebVisu (direct variable access)
| WEBVISU_OUTPUT_TOTAL_ACTIVE_POWER | DUT_Union_Real_Word |  |  | ADM100W Total Active Power | WebVisu (direct variable access)
| WEBVISU_OUTPUT_TOTAL_APPARENT_POWER | DUT_Union_Real_Word |  |  | ADM100W Total Apparent Power | WebVisu (direct variable access)
| WEBVISU_OUTPUT_TOTAL_REACTIVE_POWER | DUT_Union_Real_Word |  |  | ADM100W Total Reactive Power | WebVisu (direct variable access)
| WEBVISU_OUTPUT_ALL_PHASE_POWER_FACTOR | DUT_Union_Real_Word |  |  | ADM100W All Phase Power Factor | WebVisu (direct variable access)
| WEBVISU_OUTPUT_LOCAL_FUXA_ACTIVE | BOOL |  |  | Effective FUXA local mode (masked by WEBVISU and HMI priority) | WebVisu (direct variable access)
| WEBVISU_OUTPUT_LOCAL_HMI_ACTIVE | BOOL |  |  | Effective HMI local mode (masked by WEBVISU priority) | WebVisu (direct variable access)
Note on A1: Comment block of the DUT. Written as [Section] in the member comment, starts a new group in the declaration. Empty = same section as the row above.
Note on B1: Member name in the DUT (CODESYS identifier : letters, digits, _ , no space). Prefixes in DUT_COM : COM_ (Modbus RTU), SCADA_ (FUXA), HMI_ (local HMI), WEBVISU_ (WebVisu).
Note on C1: IEC type of the member : elementary type, DUT, function block or ARRAY[a..b] OF type (type it by hand, the list is a guide).
Note on D1: Initial value in the DUT declaration ( := value ). Empty = type default (FALSE, 0). In DUT_PA : default parameter value, used at first download and after Reset origin.
Note on E1: Engineering unit of the value (free text).
Note on F1: Comment of the member in the DUT declaration ( // ... ).
Note on G1: Where the member is exchanged : Modbus TCP (FUXA / HMI), Modbus RTU, WebVisu, physical I/O, GFC_EXC, GVL_PA, or nothing (internal).

## DUT_EXC
Section | Member | Type | Default value | Unit | Comment | Exchange
EXC : to other equipment | EXC_OUTPUT_FREQUENCY | REAL |  |  | Hz | Exchange (GFC_EXC)
| EXC_OUTPUT_L1_N_VOLTAGE | REAL |  |  | V | Exchange (GFC_EXC)
| EXC_OUTPUT_L1_CURRENT | REAL |  |  | A | Exchange (GFC_EXC)
| EXC_OUTPUT_L1_ACTIVE_POWER | REAL |  |  | W | Exchange (GFC_EXC)
| EXC_OUTPUT_L1_APPARENT_POWER | REAL |  |  | VA | Exchange (GFC_EXC)
| EXC_OUTPUT_L1_REACTIVE_POWER | REAL |  |  | VAr | Exchange (GFC_EXC)
| EXC_OUTPUT_L1_POWER_FACTOR | REAL |  |  | - | Exchange (GFC_EXC)
| EXC_OUTPUT_L1_VOLTAGE_THD | REAL |  |  | % | Exchange (GFC_EXC)
| EXC_OUTPUT_L1_CURRENT_THD | REAL |  |  | % | Exchange (GFC_EXC)
| EXC_OUTPUT_L1_MAX_LOAD | REAL |  |  | % of 60 A | Exchange (GFC_EXC)
| EXC_OUTPUT_INTERNAL_TEMPERATURE | REAL |  |  | degC | Exchange (GFC_EXC)
| EXC_OUTPUT_ACTIVE_ENERGY | REAL |  |  | kWh | Exchange (GFC_EXC)
| EXC_OUTPUT_DATA_VALID | BOOL |  |  | FALSE = values not usable. Not managed yet (no Modbus diagnostic) | Exchange (GFC_EXC)
UPI : functional units to equipment | UPI_INPUT_GLOBAL_LOCAL_FUXA | BOOL |  |  | From UPI_LOCAL_FUXA : global FUXA local active | Exchange (GFC_EXC)
| UPI_INPUT_GLOBAL_LOCAL_HMI | BOOL |  |  | From UPI_LOCAL_HMI : global HMI local active | Exchange (GFC_EXC)
| UPI_INPUT_GLOBAL_LOCAL_WEBVISU | BOOL |  |  | From UPI_LOCAL_WEBVISU : global WEBVISU local active | Exchange (GFC_EXC)
Note on A1: Comment block of the DUT. Written as [Section] in the member comment, starts a new group in the declaration. Empty = same section as the row above.
Note on B1: Member name in the DUT (CODESYS identifier : letters, digits, _ , no space). Prefixes in DUT_COM : COM_ (Modbus RTU), SCADA_ (FUXA), HMI_ (local HMI), WEBVISU_ (WebVisu).
Note on C1: IEC type of the member : elementary type, DUT, function block or ARRAY[a..b] OF type (type it by hand, the list is a guide).
Note on D1: Initial value in the DUT declaration ( := value ). Empty = type default (FALSE, 0). In DUT_PA : default parameter value, used at first download and after Reset origin.
Note on E1: Engineering unit of the value (free text).
Note on F1: Comment of the member in the DUT declaration ( // ... ).
Note on G1: Where the member is exchanged : Modbus TCP (FUXA / HMI), Modbus RTU, WebVisu, physical I/O, GFC_EXC, GVL_PA, or nothing (internal).

## DUT_INT
Section | Member | Type | Default value | Unit | Comment | Exchange
Control mode | FUXA_LOCAL_REQUEST | BOOL |  |  | From FUXA : local request (pulse or maintained)
| FUXA_AUTO_REQUEST | BOOL |  |  | From FUXA : auto request, releases the individual FUXA local
| HMI_LOCAL_REQUEST | BOOL |  |  | From HMI : local request (pulse or maintained)
| HMI_AUTO_REQUEST | BOOL |  |  | From HMI : auto request, releases the individual HMI local
| GLOBAL_LOCAL_FUXA | BOOL |  |  | From UPI_LOCAL_FUXA : global FUXA local active
| GLOBAL_LOCAL_HMI | BOOL |  |  | From UPI_LOCAL_HMI : global HMI local active
| LOCAL_FUXA_INDIVIDUAL | BOOL |  |  | Memory : individual FUXA local, set by local request, reset by auto request
| LOCAL_HMI_INDIVIDUAL | BOOL |  |  | Memory : individual HMI local, set by local request, reset by auto request
| LOCAL_HMI | BOOL |  |  | Result : equipment in HMI local (individual or global), unless WEBVISU local is active
| LOCAL_FUXA | BOOL |  |  | Result : equipment in FUXA local (individual or global), unless WEBVISU or HMI local is active
| AUTO | BOOL |  |  | Result : no local mode, commands come from the functional units (UPI)
Alarms | ALARM_1 | BOOL |  |  | Alarm 1 status
| ALARM_2 | BOOL |  |  | Alarm 2 status
| ALARM_3 | BOOL |  |  | Alarm 3 status
| ALARM_4 | BOOL |  |  | Alarm 4 status
| ALARM_5 | BOOL |  |  | Alarm 5 status
| ALARM_6 | BOOL |  |  | Alarm 6 status
| ALARM_7 | BOOL |  |  | Alarm 7 status
| ALARM_8 | BOOL |  |  | Alarm 8 status
| ALARM_9 | BOOL |  |  | Alarm 9 status
| ALARM_10 | BOOL |  |  | Alarm 10 status
Measures | FREQUENCY | REAL |  |  | Frequency ¦ Hz
| L1_L2_VOLTAGE | REAL |  |  | L1-L2 Voltage ¦ V
| L1_N_VOLTAGE | REAL |  |  | L1-N Voltage ¦ V
| L1_CURRENT | REAL |  |  | L1 Current ¦ A
| L1_ACTIVE_POWER | REAL |  |  | L1 Active Power ¦ W
| L1_APPARENT_POWER | REAL |  |  | L1 Apparent Power ¦ VA
| L1_REACTIVE_POWER | REAL |  |  | L1 Reactive Power ¦ W
| L1_CURRENT_PHASE_ANGLE | REAL |  |  | L1 Current Phase Angle ¦ deg
| L1_POWER_FACTOR | REAL |  |  | L1 Power Factor ¦ -
| L1_VOLTAGE_THD | REAL |  |  | L1 Voltage THD ¦ %
| L1_CURRENT_THD | REAL |  |  | L1 Current THD ¦ %
| L1_MAX_LOAD | REAL |  |  | L1 Max Load ¦ % of 60 A
| L1_L2_VOLTAGE_PHASE_ANGLE | REAL |  |  | L1-L2 Voltage Phase Angle ¦ deg
| L2_L3_VOLTAGE | REAL |  |  | L2-L3 Voltage ¦ V
| L2_N_VOLTAGE | REAL |  |  | L2-N Voltage ¦ V
| L2_CURRENT | REAL |  |  | L2 Current ¦ A
| L2_ACTIVE_POWER | REAL |  |  | L2 Active Power ¦ W
| L2_APPARENT_POWER | REAL |  |  | L2 Apparent Power ¦ VA
| L2_REACTIVE_POWER | REAL |  |  | L2 Reactive Power ¦ W
| L2_CURRENT_PHASE_ANGLE | REAL |  |  | L2 Current Phase Angle ¦ deg
| L2_POWER_FACTOR | REAL |  |  | L2 Power Factor ¦ -
| L2_VOLTAGE_THD | REAL |  |  | L2 Voltage THD ¦ %
| L2_CURRENT_THD | REAL |  |  | L2 Current THD ¦ %
| L2_MAX_LOAD | REAL |  |  | L2 Max Load ¦ % of 60 A
| L1_L3_VOLTAGE_PHASE_ANGLE | REAL |  |  | L1-L3 Voltage Phase Angle ¦ deg
| L3_L1_VOLTAGE | REAL |  |  | L3-L1 Voltage ¦ V
| L3_N_VOLTAGE | REAL |  |  | L3-N Voltage ¦ V
| L3_CURRENT | REAL |  |  | L3 Current ¦ A
| L3_ACTIVE_POWER | REAL |  |  | L3 Active Power ¦ W
| L3_APPARENT_POWER | REAL |  |  | L3 Apparent Power ¦ VA
| L3_REACTIVE_POWER | REAL |  |  | L3 Reactive Power ¦ W
| L3_CURRENT_PHASE_ANGLE | REAL |  |  | L3 Current Phase Angle ¦ deg
| L3_POWER_FACTOR | REAL |  |  | L3 Power Factor ¦ -
| L3_VOLTAGE_THD | REAL |  |  | L3 Voltage THD ¦ %
| L3_CURRENT_THD | REAL |  |  | L3 Current THD ¦ %
| L3_MAX_LOAD | REAL |  |  | L3 Max Load ¦ % of 60 A
| INTERNAL_TEMPERATURE | REAL |  |  | Internal Temperature ¦ degC
| ACTIVE_ENERGY | REAL |  |  | Active Energy ¦ kWh
| APPARENT_ENERGY | REAL |  |  | Apparent Energy ¦ per ADM100W config
| REACTIVE_ENERGY | REAL |  |  | Reactive Energy ¦ kWh
| TOTAL_ACTIVE_POWER | REAL |  |  | Total Active Power ¦ W
| TOTAL_APPARENT_POWER | REAL |  |  | Total Apparent Power ¦ VA
| TOTAL_REACTIVE_POWER | REAL |  |  | Total Reactive Power ¦ W
| ALL_PHASE_POWER_FACTOR | REAL |  |  | All Phase Power Factor ¦ -
| WEBVISU_LOCAL_REQUEST | BOOL |  |  | From WEBVISU : individual local request
| WEBVISU_AUTO_REQUEST | BOOL |  |  | From WEBVISU : releases individual WEBVISU local (auto wins)
| GLOBAL_LOCAL_WEBVISU | BOOL |  |  | From UPI_LOCAL_WEBVISU : global local request
| LOCAL_WEBVISU_INDIVIDUAL | BOOL |  |  | Memory : individual WEBVISU local request
| LOCAL_WEBVISU | BOOL |  |  | Effective WEBVISU local : highest source priority
Note on A1: Comment block of the DUT. Written as [Section] in the member comment, starts a new group in the declaration. Empty = same section as the row above.
Note on B1: Member name in the DUT (CODESYS identifier : letters, digits, _ , no space). Prefixes in DUT_COM : COM_ (Modbus RTU), SCADA_ (FUXA), HMI_ (local HMI), WEBVISU_ (WebVisu).
Note on C1: IEC type of the member : elementary type, DUT, function block or ARRAY[a..b] OF type (type it by hand, the list is a guide).
Note on D1: Initial value in the DUT declaration ( := value ). Empty = type default (FALSE, 0). In DUT_PA : default parameter value, used at first download and after Reset origin.
Note on E1: Engineering unit of the value (free text).
Note on F1: Comment of the member in the DUT declaration ( // ... ).
Note on G1: Where the member is exchanged : Modbus TCP (FUXA / HMI), Modbus RTU, WebVisu, physical I/O, GFC_EXC, GVL_PA, or nothing (internal).

## DUT_IO
Section | Member | Type | Default value | Unit | Comment | Exchange
| SPARE | BOOL |  |  | Placeholder, structure not used yet
Note on A1: Comment block of the DUT. Written as [Section] in the member comment, starts a new group in the declaration. Empty = same section as the row above.
Note on B1: Member name in the DUT (CODESYS identifier : letters, digits, _ , no space). Prefixes in DUT_COM : COM_ (Modbus RTU), SCADA_ (FUXA), HMI_ (local HMI), WEBVISU_ (WebVisu).
Note on C1: IEC type of the member : elementary type, DUT, function block or ARRAY[a..b] OF type (type it by hand, the list is a guide).
Note on D1: Initial value in the DUT declaration ( := value ). Empty = type default (FALSE, 0). In DUT_PA : default parameter value, used at first download and after Reset origin.
Note on E1: Engineering unit of the value (free text).
Note on F1: Comment of the member in the DUT declaration ( // ... ).
Note on G1: Where the member is exchanged : Modbus TCP (FUXA / HMI), Modbus RTU, WebVisu, physical I/O, GFC_EXC, GVL_PA, or nothing (internal).

## DUT_PA
Section | Member | Type | Default value | Unit | Comment | Exchange
| SPARE | BOOL |  |  | Placeholder, structure not used yet
Note on A1: Comment block of the DUT. Written as [Section] in the member comment, starts a new group in the declaration. Empty = same section as the row above.
Note on B1: Member name in the DUT (CODESYS identifier : letters, digits, _ , no space). Prefixes in DUT_COM : COM_ (Modbus RTU), SCADA_ (FUXA), HMI_ (local HMI), WEBVISU_ (WebVisu).
Note on C1: IEC type of the member : elementary type, DUT, function block or ARRAY[a..b] OF type (type it by hand, the list is a guide).
Note on D1: Initial value in the DUT declaration ( := value ). Empty = type default (FALSE, 0). In DUT_PA : default parameter value, used at first download and after Reset origin.
Note on E1: Engineering unit of the value (free text).
Note on F1: Comment of the member in the DUT declaration ( // ... ).
Note on G1: Where the member is exchanged : Modbus TCP (FUXA / HMI), Modbus RTU, WebVisu, physical I/O, GFC_EXC, GVL_PA, or nothing (internal).

## RTU_DEFAULT
Key | Value | Comment
Interface | RS-485
Factory slave address | TO CHECK
Factory baud rate | TO CHECK
Supported baud rates | TO CHECK
32-bit word order | ABCD (MSW first)
Read channels | Cyclic
Write channels | None (read only)
Setup on the equipment | TO CHECK
Note on A1: Name of the setting. Do not change it, the generator reads the value by this key.
Note on B1: Value of the setting. Use the drop-down list when there is one.
Note on C1: Free text. Not used by the generator.

## RTU_COILS
Equipment address | Channel offset | Function | Direction | Name | Type | Word | Word order | Scale | Unit | DUT_COM member | CODESYS channel | Comment
0 | 0 | FC01 Read Coils | Equipment to PLC | ADM100W Alarm 1 Status | BOOL |  |  |  |  | COM_INPUT_COILS[0].0 | Read, cyclic
1 | 1 | FC01 Read Coils | Equipment to PLC | ADM100W Alarm 2 Status | BOOL |  |  |  |  | COM_INPUT_COILS[0].1 | Read, cyclic
2 | 2 | FC01 Read Coils | Equipment to PLC | ADM100W Alarm 3 Status | BOOL |  |  |  |  | COM_INPUT_COILS[0].2 | Read, cyclic
3 | 3 | FC01 Read Coils | Equipment to PLC | ADM100W Alarm 4 Status | BOOL |  |  |  |  | COM_INPUT_COILS[0].3 | Read, cyclic
4 | 4 | FC01 Read Coils | Equipment to PLC | ADM100W Alarm 5 Status | BOOL |  |  |  |  | COM_INPUT_COILS[0].4 | Read, cyclic
5 | 5 | FC01 Read Coils | Equipment to PLC | ADM100W Alarm 6 Status | BOOL |  |  |  |  | COM_INPUT_COILS[0].5 | Read, cyclic
6 | 6 | FC01 Read Coils | Equipment to PLC | ADM100W Alarm 7 Status | BOOL |  |  |  |  | COM_INPUT_COILS[0].6 | Read, cyclic
7 | 7 | FC01 Read Coils | Equipment to PLC | ADM100W Alarm 8 Status | BOOL |  |  |  |  | COM_INPUT_COILS[0].7 | Read, cyclic
8 | 8 | FC01 Read Coils | Equipment to PLC | ADM100W Alarm 9 Status | BOOL |  |  |  |  | COM_INPUT_COILS[1].0 | Read, cyclic
9 | 9 | FC01 Read Coils | Equipment to PLC | ADM100W Alarm 10 Status | BOOL |  |  |  |  | COM_INPUT_COILS[1].1 | Read, cyclic
Note on A1: Register or coil address as written in the equipment manual (hex 0x4001 or decimal).
Note on B1: Position in the CODESYS Modbus channel and in the GVL_MODBUS array (0 = first register of the channel).
Note on C1: Modbus function code used by the CODESYS channel.
Note on D1: Equipment to PLC = read by the PLC. PLC to Equipment = written by the PLC.
Note on E1: Readable name of the value. Used as tag name in FUXA and as label in the supervisions.
Note on F1: Type of the value in the equipment. 32-bit values use 2 rows.
Note on G1: 32-bit value split in 2 registers : MSW = most significant word, LSW = least significant word. Empty for 16-bit and BOOL.
Note on H1: Order of the 2 words in the equipment : ABCD = MSW at the lower address, CDAB = LSW at the lower address.
Note on I1: Conversion raw value -> engineering value, as written in the equipment manual. "1" = no conversion.
Note on J1: Engineering unit of the value (free text).
Note on K1: Member of DUT_COM_<type> that receives (read) or provides (write) the value, copied by GFC_COM_IN / GFC_COM_OUT.
Note on L1: How the CODESYS Modbus master channel runs : cyclic, or on the rising edge of a trigger variable mapped in the slave I/O mapping.
Note on M1: Free text. Not used by the generator.

## RTU_DI
Equipment address | Channel offset | Function | Direction | Name | Type | Word | Word order | Scale | Unit | DUT_COM member | CODESYS channel | Comment
Note on A1: Register or coil address as written in the equipment manual (hex 0x4001 or decimal).
Note on B1: Position in the CODESYS Modbus channel and in the GVL_MODBUS array (0 = first register of the channel).
Note on C1: Modbus function code used by the CODESYS channel.
Note on D1: Equipment to PLC = read by the PLC. PLC to Equipment = written by the PLC.
Note on E1: Readable name of the value. Used as tag name in FUXA and as label in the supervisions.
Note on F1: Type of the value in the equipment. 32-bit values use 2 rows.
Note on G1: 32-bit value split in 2 registers : MSW = most significant word, LSW = least significant word. Empty for 16-bit and BOOL.
Note on H1: Order of the 2 words in the equipment : ABCD = MSW at the lower address, CDAB = LSW at the lower address.
Note on I1: Conversion raw value -> engineering value, as written in the equipment manual. "1" = no conversion.
Note on J1: Engineering unit of the value (free text).
Note on K1: Member of DUT_COM_<type> that receives (read) or provides (write) the value, copied by GFC_COM_IN / GFC_COM_OUT.
Note on L1: How the CODESYS Modbus master channel runs : cyclic, or on the rising edge of a trigger variable mapped in the slave I/O mapping.
Note on M1: Free text. Not used by the generator.

## RTU_IR
Equipment address | Channel offset | Function | Direction | Name | Type | Word | Word order | Scale | Unit | DUT_COM member | CODESYS channel | Comment
0 | 0 | FC04 Read Input Registers | Equipment to PLC | ADM100W Frequency | REAL | MSW | ABCD (MSW first) | 1 | Hz | COM_INPUT_IR[0] | Read, cyclic
1 | 1 | FC04 Read Input Registers | Equipment to PLC | ADM100W Frequency | REAL | LSW | ABCD (MSW first) | 1 | Hz | COM_INPUT_IR[1] | Read, cyclic
2 | 2 | FC04 Read Input Registers | Equipment to PLC | ADM100W L1-L2 Voltage | REAL | MSW | ABCD (MSW first) | 1 | V | COM_INPUT_IR[2] | Read, cyclic
3 | 3 | FC04 Read Input Registers | Equipment to PLC | ADM100W L1-L2 Voltage | REAL | LSW | ABCD (MSW first) | 1 | V | COM_INPUT_IR[3] | Read, cyclic
4 | 4 | FC04 Read Input Registers | Equipment to PLC | ADM100W L1-N Voltage | REAL | MSW | ABCD (MSW first) | 1 | V | COM_INPUT_IR[4] | Read, cyclic
5 | 5 | FC04 Read Input Registers | Equipment to PLC | ADM100W L1-N Voltage | REAL | LSW | ABCD (MSW first) | 1 | V | COM_INPUT_IR[5] | Read, cyclic
6 | 6 | FC04 Read Input Registers | Equipment to PLC | ADM100W L1 Current | REAL | MSW | ABCD (MSW first) | 1 | A | COM_INPUT_IR[6] | Read, cyclic
7 | 7 | FC04 Read Input Registers | Equipment to PLC | ADM100W L1 Current | REAL | LSW | ABCD (MSW first) | 1 | A | COM_INPUT_IR[7] | Read, cyclic
8 | 8 | FC04 Read Input Registers | Equipment to PLC | ADM100W L1 Active Power | REAL | MSW | ABCD (MSW first) | 1 | per ADM100W config | COM_INPUT_IR[8] | Read, cyclic
9 | 9 | FC04 Read Input Registers | Equipment to PLC | ADM100W L1 Active Power | REAL | LSW | ABCD (MSW first) | 1 | per ADM100W config | COM_INPUT_IR[9] | Read, cyclic
10 | 10 | FC04 Read Input Registers | Equipment to PLC | ADM100W L1 Apparent Power | REAL | MSW | ABCD (MSW first) | 1 | per ADM100W config | COM_INPUT_IR[10] | Read, cyclic
11 | 11 | FC04 Read Input Registers | Equipment to PLC | ADM100W L1 Apparent Power | REAL | LSW | ABCD (MSW first) | 1 | per ADM100W config | COM_INPUT_IR[11] | Read, cyclic
12 | 12 | FC04 Read Input Registers | Equipment to PLC | ADM100W L1 Reactive Power | REAL | MSW | ABCD (MSW first) | 1 | per ADM100W config | COM_INPUT_IR[12] | Read, cyclic
13 | 13 | FC04 Read Input Registers | Equipment to PLC | ADM100W L1 Reactive Power | REAL | LSW | ABCD (MSW first) | 1 | per ADM100W config | COM_INPUT_IR[13] | Read, cyclic
14 | 14 | FC04 Read Input Registers | Equipment to PLC | ADM100W L1 Current Phase Angle | REAL | MSW | ABCD (MSW first) | 1 | ° | COM_INPUT_IR[14] | Read, cyclic
15 | 15 | FC04 Read Input Registers | Equipment to PLC | ADM100W L1 Current Phase Angle | REAL | LSW | ABCD (MSW first) | 1 | ° | COM_INPUT_IR[15] | Read, cyclic
16 | 16 | FC04 Read Input Registers | Equipment to PLC | ADM100W L1 Power Factor | REAL | MSW | ABCD (MSW first) | 1 |  | COM_INPUT_IR[16] | Read, cyclic
17 | 17 | FC04 Read Input Registers | Equipment to PLC | ADM100W L1 Power Factor | REAL | LSW | ABCD (MSW first) | 1 |  | COM_INPUT_IR[17] | Read, cyclic
18 | 18 | FC04 Read Input Registers | Equipment to PLC | ADM100W L1 Voltage THD | REAL | MSW | ABCD (MSW first) | 1 | % | COM_INPUT_IR[18] | Read, cyclic
19 | 19 | FC04 Read Input Registers | Equipment to PLC | ADM100W L1 Voltage THD | REAL | LSW | ABCD (MSW first) | 1 | % | COM_INPUT_IR[19] | Read, cyclic
20 | 20 | FC04 Read Input Registers | Equipment to PLC | ADM100W L1 Current THD | REAL | MSW | ABCD (MSW first) | 1 | % | COM_INPUT_IR[20] | Read, cyclic
21 | 21 | FC04 Read Input Registers | Equipment to PLC | ADM100W L1 Current THD | REAL | LSW | ABCD (MSW first) | 1 | % | COM_INPUT_IR[21] | Read, cyclic
22 | 22 | FC04 Read Input Registers | Equipment to PLC | ADM100W L1 Max Load | REAL | MSW | ABCD (MSW first) | 1 | per ADM100W config | COM_INPUT_IR[22] | Read, cyclic
23 | 23 | FC04 Read Input Registers | Equipment to PLC | ADM100W L1 Max Load | REAL | LSW | ABCD (MSW first) | 1 | per ADM100W config | COM_INPUT_IR[23] | Read, cyclic
24 | 24 | FC04 Read Input Registers | Equipment to PLC | ADM100W L1-L2 Voltage Phase Angle | REAL | MSW | ABCD (MSW first) | 1 | ° | COM_INPUT_IR[24] | Read, cyclic
25 | 25 | FC04 Read Input Registers | Equipment to PLC | ADM100W L1-L2 Voltage Phase Angle | REAL | LSW | ABCD (MSW first) | 1 | ° | COM_INPUT_IR[25] | Read, cyclic
26 | 26 | FC04 Read Input Registers | Equipment to PLC | ADM100W L2-L3 Voltage | REAL | MSW | ABCD (MSW first) | 1 | V | COM_INPUT_IR[26] | Read, cyclic
27 | 27 | FC04 Read Input Registers | Equipment to PLC | ADM100W L2-L3 Voltage | REAL | LSW | ABCD (MSW first) | 1 | V | COM_INPUT_IR[27] | Read, cyclic
28 | 28 | FC04 Read Input Registers | Equipment to PLC | ADM100W L2-N Voltage | REAL | MSW | ABCD (MSW first) | 1 | V | COM_INPUT_IR[28] | Read, cyclic
29 | 29 | FC04 Read Input Registers | Equipment to PLC | ADM100W L2-N Voltage | REAL | LSW | ABCD (MSW first) | 1 | V | COM_INPUT_IR[29] | Read, cyclic
30 | 30 | FC04 Read Input Registers | Equipment to PLC | ADM100W L2 Current | REAL | MSW | ABCD (MSW first) | 1 | A | COM_INPUT_IR[30] | Read, cyclic
31 | 31 | FC04 Read Input Registers | Equipment to PLC | ADM100W L2 Current | REAL | LSW | ABCD (MSW first) | 1 | A | COM_INPUT_IR[31] | Read, cyclic
32 | 32 | FC04 Read Input Registers | Equipment to PLC | ADM100W L2 Active Power | REAL | MSW | ABCD (MSW first) | 1 | per ADM100W config | COM_INPUT_IR[32] | Read, cyclic
33 | 33 | FC04 Read Input Registers | Equipment to PLC | ADM100W L2 Active Power | REAL | LSW | ABCD (MSW first) | 1 | per ADM100W config | COM_INPUT_IR[33] | Read, cyclic
34 | 34 | FC04 Read Input Registers | Equipment to PLC | ADM100W L2 Apparent Power | REAL | MSW | ABCD (MSW first) | 1 | per ADM100W config | COM_INPUT_IR[34] | Read, cyclic
35 | 35 | FC04 Read Input Registers | Equipment to PLC | ADM100W L2 Apparent Power | REAL | LSW | ABCD (MSW first) | 1 | per ADM100W config | COM_INPUT_IR[35] | Read, cyclic
36 | 36 | FC04 Read Input Registers | Equipment to PLC | ADM100W L2 Reactive Power | REAL | MSW | ABCD (MSW first) | 1 | per ADM100W config | COM_INPUT_IR[36] | Read, cyclic
37 | 37 | FC04 Read Input Registers | Equipment to PLC | ADM100W L2 Reactive Power | REAL | LSW | ABCD (MSW first) | 1 | per ADM100W config | COM_INPUT_IR[37] | Read, cyclic
38 | 38 | FC04 Read Input Registers | Equipment to PLC | ADM100W L2 Current Phase Angle | REAL | MSW | ABCD (MSW first) | 1 | ° | COM_INPUT_IR[38] | Read, cyclic
39 | 39 | FC04 Read Input Registers | Equipment to PLC | ADM100W L2 Current Phase Angle | REAL | LSW | ABCD (MSW first) | 1 | ° | COM_INPUT_IR[39] | Read, cyclic
40 | 40 | FC04 Read Input Registers | Equipment to PLC | ADM100W L2 Power Factor | REAL | MSW | ABCD (MSW first) | 1 |  | COM_INPUT_IR[40] | Read, cyclic
41 | 41 | FC04 Read Input Registers | Equipment to PLC | ADM100W L2 Power Factor | REAL | LSW | ABCD (MSW first) | 1 |  | COM_INPUT_IR[41] | Read, cyclic
42 | 42 | FC04 Read Input Registers | Equipment to PLC | ADM100W L2 Voltage THD | REAL | MSW | ABCD (MSW first) | 1 | % | COM_INPUT_IR[42] | Read, cyclic
43 | 43 | FC04 Read Input Registers | Equipment to PLC | ADM100W L2 Voltage THD | REAL | LSW | ABCD (MSW first) | 1 | % | COM_INPUT_IR[43] | Read, cyclic
44 | 44 | FC04 Read Input Registers | Equipment to PLC | ADM100W L2 Current THD | REAL | MSW | ABCD (MSW first) | 1 | % | COM_INPUT_IR[44] | Read, cyclic
45 | 45 | FC04 Read Input Registers | Equipment to PLC | ADM100W L2 Current THD | REAL | LSW | ABCD (MSW first) | 1 | % | COM_INPUT_IR[45] | Read, cyclic
46 | 46 | FC04 Read Input Registers | Equipment to PLC | ADM100W L2 Max Load | REAL | MSW | ABCD (MSW first) | 1 | per ADM100W config | COM_INPUT_IR[46] | Read, cyclic
47 | 47 | FC04 Read Input Registers | Equipment to PLC | ADM100W L2 Max Load | REAL | LSW | ABCD (MSW first) | 1 | per ADM100W config | COM_INPUT_IR[47] | Read, cyclic
48 | 48 | FC04 Read Input Registers | Equipment to PLC | ADM100W L1-L3 Voltage Phase Angle | REAL | MSW | ABCD (MSW first) | 1 | ° | COM_INPUT_IR[48] | Read, cyclic
49 | 49 | FC04 Read Input Registers | Equipment to PLC | ADM100W L1-L3 Voltage Phase Angle | REAL | LSW | ABCD (MSW first) | 1 | ° | COM_INPUT_IR[49] | Read, cyclic
50 | 50 | FC04 Read Input Registers | Equipment to PLC | ADM100W L3-L1 Voltage | REAL | MSW | ABCD (MSW first) | 1 | V | COM_INPUT_IR[50] | Read, cyclic
51 | 51 | FC04 Read Input Registers | Equipment to PLC | ADM100W L3-L1 Voltage | REAL | LSW | ABCD (MSW first) | 1 | V | COM_INPUT_IR[51] | Read, cyclic
52 | 52 | FC04 Read Input Registers | Equipment to PLC | ADM100W L3-N Voltage | REAL | MSW | ABCD (MSW first) | 1 | V | COM_INPUT_IR[52] | Read, cyclic
53 | 53 | FC04 Read Input Registers | Equipment to PLC | ADM100W L3-N Voltage | REAL | LSW | ABCD (MSW first) | 1 | V | COM_INPUT_IR[53] | Read, cyclic
54 | 54 | FC04 Read Input Registers | Equipment to PLC | ADM100W L3 Current | REAL | MSW | ABCD (MSW first) | 1 | A | COM_INPUT_IR[54] | Read, cyclic
55 | 55 | FC04 Read Input Registers | Equipment to PLC | ADM100W L3 Current | REAL | LSW | ABCD (MSW first) | 1 | A | COM_INPUT_IR[55] | Read, cyclic
56 | 56 | FC04 Read Input Registers | Equipment to PLC | ADM100W L3 Active Power | REAL | MSW | ABCD (MSW first) | 1 | per ADM100W config | COM_INPUT_IR[56] | Read, cyclic
57 | 57 | FC04 Read Input Registers | Equipment to PLC | ADM100W L3 Active Power | REAL | LSW | ABCD (MSW first) | 1 | per ADM100W config | COM_INPUT_IR[57] | Read, cyclic
58 | 58 | FC04 Read Input Registers | Equipment to PLC | ADM100W L3 Apparent Power | REAL | MSW | ABCD (MSW first) | 1 | per ADM100W config | COM_INPUT_IR[58] | Read, cyclic
59 | 59 | FC04 Read Input Registers | Equipment to PLC | ADM100W L3 Apparent Power | REAL | LSW | ABCD (MSW first) | 1 | per ADM100W config | COM_INPUT_IR[59] | Read, cyclic
60 | 60 | FC04 Read Input Registers | Equipment to PLC | ADM100W L3 Reactive Power | REAL | MSW | ABCD (MSW first) | 1 | per ADM100W config | COM_INPUT_IR[60] | Read, cyclic
61 | 61 | FC04 Read Input Registers | Equipment to PLC | ADM100W L3 Reactive Power | REAL | LSW | ABCD (MSW first) | 1 | per ADM100W config | COM_INPUT_IR[61] | Read, cyclic
62 | 62 | FC04 Read Input Registers | Equipment to PLC | ADM100W L3 Current Phase Angle | REAL | MSW | ABCD (MSW first) | 1 | ° | COM_INPUT_IR[62] | Read, cyclic
63 | 63 | FC04 Read Input Registers | Equipment to PLC | ADM100W L3 Current Phase Angle | REAL | LSW | ABCD (MSW first) | 1 | ° | COM_INPUT_IR[63] | Read, cyclic
64 | 64 | FC04 Read Input Registers | Equipment to PLC | ADM100W L3 Power Factor | REAL | MSW | ABCD (MSW first) | 1 |  | COM_INPUT_IR[64] | Read, cyclic
65 | 65 | FC04 Read Input Registers | Equipment to PLC | ADM100W L3 Power Factor | REAL | LSW | ABCD (MSW first) | 1 |  | COM_INPUT_IR[65] | Read, cyclic
66 | 66 | FC04 Read Input Registers | Equipment to PLC | ADM100W L3 Voltage THD | REAL | MSW | ABCD (MSW first) | 1 | % | COM_INPUT_IR[66] | Read, cyclic
67 | 67 | FC04 Read Input Registers | Equipment to PLC | ADM100W L3 Voltage THD | REAL | LSW | ABCD (MSW first) | 1 | % | COM_INPUT_IR[67] | Read, cyclic
68 | 68 | FC04 Read Input Registers | Equipment to PLC | ADM100W L3 Current THD | REAL | MSW | ABCD (MSW first) | 1 | % | COM_INPUT_IR[68] | Read, cyclic
69 | 69 | FC04 Read Input Registers | Equipment to PLC | ADM100W L3 Current THD | REAL | LSW | ABCD (MSW first) | 1 | % | COM_INPUT_IR[69] | Read, cyclic
70 | 70 | FC04 Read Input Registers | Equipment to PLC | ADM100W L3 Max Load | REAL | MSW | ABCD (MSW first) | 1 | per ADM100W config | COM_INPUT_IR[70] | Read, cyclic
71 | 71 | FC04 Read Input Registers | Equipment to PLC | ADM100W L3 Max Load | REAL | LSW | ABCD (MSW first) | 1 | per ADM100W config | COM_INPUT_IR[71] | Read, cyclic
72 | 72 | FC04 Read Input Registers | Equipment to PLC | ADM100W Internal Temperature | REAL | MSW | ABCD (MSW first) | 1 | per ADM100W config | COM_INPUT_IR[72] | Read, cyclic
73 | 73 | FC04 Read Input Registers | Equipment to PLC | ADM100W Internal Temperature | REAL | LSW | ABCD (MSW first) | 1 | per ADM100W config | COM_INPUT_IR[73] | Read, cyclic
74 | 74 | FC04 Read Input Registers | Equipment to PLC | ADM100W Active Energy | REAL | MSW | ABCD (MSW first) | 1 | per ADM100W config | COM_INPUT_IR[74] | Read, cyclic
75 | 75 | FC04 Read Input Registers | Equipment to PLC | ADM100W Active Energy | REAL | LSW | ABCD (MSW first) | 1 | per ADM100W config | COM_INPUT_IR[75] | Read, cyclic
76 | 76 | FC04 Read Input Registers | Equipment to PLC | ADM100W Apparent Energy | REAL | MSW | ABCD (MSW first) | 1 | per ADM100W config | COM_INPUT_IR[76] | Read, cyclic
77 | 77 | FC04 Read Input Registers | Equipment to PLC | ADM100W Apparent Energy | REAL | LSW | ABCD (MSW first) | 1 | per ADM100W config | COM_INPUT_IR[77] | Read, cyclic
78 | 78 | FC04 Read Input Registers | Equipment to PLC | ADM100W Reactive Energy | REAL | MSW | ABCD (MSW first) | 1 | per ADM100W config | COM_INPUT_IR[78] | Read, cyclic
79 | 79 | FC04 Read Input Registers | Equipment to PLC | ADM100W Reactive Energy | REAL | LSW | ABCD (MSW first) | 1 | per ADM100W config | COM_INPUT_IR[79] | Read, cyclic
80 | 80 | FC04 Read Input Registers | Equipment to PLC | ADM100W Total Active Power | REAL | MSW | ABCD (MSW first) | 1 | per ADM100W config | COM_INPUT_IR[80] | Read, cyclic
81 | 81 | FC04 Read Input Registers | Equipment to PLC | ADM100W Total Active Power | REAL | LSW | ABCD (MSW first) | 1 | per ADM100W config | COM_INPUT_IR[81] | Read, cyclic
82 | 82 | FC04 Read Input Registers | Equipment to PLC | ADM100W Total Apparent Power | REAL | MSW | ABCD (MSW first) | 1 | per ADM100W config | COM_INPUT_IR[82] | Read, cyclic
83 | 83 | FC04 Read Input Registers | Equipment to PLC | ADM100W Total Apparent Power | REAL | LSW | ABCD (MSW first) | 1 | per ADM100W config | COM_INPUT_IR[83] | Read, cyclic
84 | 84 | FC04 Read Input Registers | Equipment to PLC | ADM100W Total Reactive Power | REAL | MSW | ABCD (MSW first) | 1 | per ADM100W config | COM_INPUT_IR[84] | Read, cyclic
85 | 85 | FC04 Read Input Registers | Equipment to PLC | ADM100W Total Reactive Power | REAL | LSW | ABCD (MSW first) | 1 | per ADM100W config | COM_INPUT_IR[85] | Read, cyclic
86 | 86 | FC04 Read Input Registers | Equipment to PLC | ADM100W All Phase Power Factor | REAL | MSW | ABCD (MSW first) | 1 |  | COM_INPUT_IR[86] | Read, cyclic
87 | 87 | FC04 Read Input Registers | Equipment to PLC | ADM100W All Phase Power Factor | REAL | LSW | ABCD (MSW first) | 1 |  | COM_INPUT_IR[87] | Read, cyclic
Note on A1: Register or coil address as written in the equipment manual (hex 0x4001 or decimal).
Note on B1: Position in the CODESYS Modbus channel and in the GVL_MODBUS array (0 = first register of the channel).
Note on C1: Modbus function code used by the CODESYS channel.
Note on D1: Equipment to PLC = read by the PLC. PLC to Equipment = written by the PLC.
Note on E1: Readable name of the value. Used as tag name in FUXA and as label in the supervisions.
Note on F1: Type of the value in the equipment. 32-bit values use 2 rows.
Note on G1: 32-bit value split in 2 registers : MSW = most significant word, LSW = least significant word. Empty for 16-bit and BOOL.
Note on H1: Order of the 2 words in the equipment : ABCD = MSW at the lower address, CDAB = LSW at the lower address.
Note on I1: Conversion raw value -> engineering value, as written in the equipment manual. "1" = no conversion.
Note on J1: Engineering unit of the value (free text).
Note on K1: Member of DUT_COM_<type> that receives (read) or provides (write) the value, copied by GFC_COM_IN / GFC_COM_OUT.
Note on L1: How the CODESYS Modbus master channel runs : cyclic, or on the rising edge of a trigger variable mapped in the slave I/O mapping.
Note on M1: Free text. Not used by the generator.

## RTU_HR
Equipment address | Channel offset | Function | Direction | Name | Type | Word | Word order | Scale | Unit | DUT_COM member | CODESYS channel | Comment
Note on A1: Register or coil address as written in the equipment manual (hex 0x4001 or decimal).
Note on B1: Position in the CODESYS Modbus channel and in the GVL_MODBUS array (0 = first register of the channel).
Note on C1: Modbus function code used by the CODESYS channel.
Note on D1: Equipment to PLC = read by the PLC. PLC to Equipment = written by the PLC.
Note on E1: Readable name of the value. Used as tag name in FUXA and as label in the supervisions.
Note on F1: Type of the value in the equipment. 32-bit values use 2 rows.
Note on G1: 32-bit value split in 2 registers : MSW = most significant word, LSW = least significant word. Empty for 16-bit and BOOL.
Note on H1: Order of the 2 words in the equipment : ABCD = MSW at the lower address, CDAB = LSW at the lower address.
Note on I1: Conversion raw value -> engineering value, as written in the equipment manual. "1" = no conversion.
Note on J1: Engineering unit of the value (free text).
Note on K1: Member of DUT_COM_<type> that receives (read) or provides (write) the value, copied by GFC_COM_IN / GFC_COM_OUT.
Note on L1: How the CODESYS Modbus master channel runs : cyclic, or on the rising edge of a trigger variable mapped in the slave I/O mapping.
Note on M1: Free text. Not used by the generator.

## TEMPLATE_PA
Member | Type | Default value | Instance value | Unit | Changed from supervision | Comment | GVL_PA variable
SPARE | BOOL |  |  |  | No | Placeholder, structure not used yet | GVL_PA.PA_<INSTANCE>.SPARE
Note on A1: Member of DUT_PA_<type>.
Note on B1: Type of the parameter in DUT_PA_<type>.
Note on C1: Declaration value in DUT_PA_<type> (TYPE file). Same for every instance.
Note on D1: Value for this instance when it differs from the default. Empty = default value. Declared in GVL_PA : PA_<instance> : DUT_PA_<type> := (MEMBER := value);
Note on E1: Engineering unit of the value (free text).
Note on F1: Yes = the FB copies a value typed in the active local supervision into GVL_PA (persistent). No = only the declaration value is used.
Note on G1: Comment of the parameter in DUT_PA_<type>.
Note on H1: Persistent variable : GVL_PA.PA_<instance>.<member> (VAR_GLOBAL PERSISTENT RETAIN).

## TEMPLATE_RTU
Table | Equipment address | Channel offset | Function | Direction | Name | Type | Word | Scale | Unit | GVL_MODBUS variable | GVL_COM variable | CODESYS channel | Comment
Coil | 0 | 0 | FC01 Read Coils | Equipment to PLC | ADM100W Alarm 1 Status | BOOL |  |  |  | GVL_MODBUS.ADM100W_Alarms[0].0 | GVL_COM.COM_<INSTANCE>.COM_INPUT_COILS[0].0 | Read, cyclic
Coil | 1 | 1 | FC01 Read Coils | Equipment to PLC | ADM100W Alarm 2 Status | BOOL |  |  |  | GVL_MODBUS.ADM100W_Alarms[0].1 | GVL_COM.COM_<INSTANCE>.COM_INPUT_COILS[0].1 | Read, cyclic
Coil | 2 | 2 | FC01 Read Coils | Equipment to PLC | ADM100W Alarm 3 Status | BOOL |  |  |  | GVL_MODBUS.ADM100W_Alarms[0].2 | GVL_COM.COM_<INSTANCE>.COM_INPUT_COILS[0].2 | Read, cyclic
Coil | 3 | 3 | FC01 Read Coils | Equipment to PLC | ADM100W Alarm 4 Status | BOOL |  |  |  | GVL_MODBUS.ADM100W_Alarms[0].3 | GVL_COM.COM_<INSTANCE>.COM_INPUT_COILS[0].3 | Read, cyclic
Coil | 4 | 4 | FC01 Read Coils | Equipment to PLC | ADM100W Alarm 5 Status | BOOL |  |  |  | GVL_MODBUS.ADM100W_Alarms[0].4 | GVL_COM.COM_<INSTANCE>.COM_INPUT_COILS[0].4 | Read, cyclic
Coil | 5 | 5 | FC01 Read Coils | Equipment to PLC | ADM100W Alarm 6 Status | BOOL |  |  |  | GVL_MODBUS.ADM100W_Alarms[0].5 | GVL_COM.COM_<INSTANCE>.COM_INPUT_COILS[0].5 | Read, cyclic
Coil | 6 | 6 | FC01 Read Coils | Equipment to PLC | ADM100W Alarm 7 Status | BOOL |  |  |  | GVL_MODBUS.ADM100W_Alarms[0].6 | GVL_COM.COM_<INSTANCE>.COM_INPUT_COILS[0].6 | Read, cyclic
Coil | 7 | 7 | FC01 Read Coils | Equipment to PLC | ADM100W Alarm 8 Status | BOOL |  |  |  | GVL_MODBUS.ADM100W_Alarms[0].7 | GVL_COM.COM_<INSTANCE>.COM_INPUT_COILS[0].7 | Read, cyclic
Coil | 8 | 8 | FC01 Read Coils | Equipment to PLC | ADM100W Alarm 9 Status | BOOL |  |  |  | GVL_MODBUS.ADM100W_Alarms[1].0 | GVL_COM.COM_<INSTANCE>.COM_INPUT_COILS[1].0 | Read, cyclic
Coil | 9 | 9 | FC01 Read Coils | Equipment to PLC | ADM100W Alarm 10 Status | BOOL |  |  |  | GVL_MODBUS.ADM100W_Alarms[1].1 | GVL_COM.COM_<INSTANCE>.COM_INPUT_COILS[1].1 | Read, cyclic
IR | 0 | 0 | FC04 Read Input Registers | Equipment to PLC | ADM100W Frequency | REAL | MSW | 1 | Hz | GVL_MODBUS.ADM100W_InputRegisters[0] | GVL_COM.COM_<INSTANCE>.COM_INPUT_IR[0] | Read, cyclic
IR | 1 | 1 | FC04 Read Input Registers | Equipment to PLC | ADM100W Frequency | REAL | LSW | 1 | Hz | GVL_MODBUS.ADM100W_InputRegisters[1] | GVL_COM.COM_<INSTANCE>.COM_INPUT_IR[1] | Read, cyclic
IR | 2 | 2 | FC04 Read Input Registers | Equipment to PLC | ADM100W L1-L2 Voltage | REAL | MSW | 1 | V | GVL_MODBUS.ADM100W_InputRegisters[2] | GVL_COM.COM_<INSTANCE>.COM_INPUT_IR[2] | Read, cyclic
IR | 3 | 3 | FC04 Read Input Registers | Equipment to PLC | ADM100W L1-L2 Voltage | REAL | LSW | 1 | V | GVL_MODBUS.ADM100W_InputRegisters[3] | GVL_COM.COM_<INSTANCE>.COM_INPUT_IR[3] | Read, cyclic
IR | 4 | 4 | FC04 Read Input Registers | Equipment to PLC | ADM100W L1-N Voltage | REAL | MSW | 1 | V | GVL_MODBUS.ADM100W_InputRegisters[4] | GVL_COM.COM_<INSTANCE>.COM_INPUT_IR[4] | Read, cyclic
IR | 5 | 5 | FC04 Read Input Registers | Equipment to PLC | ADM100W L1-N Voltage | REAL | LSW | 1 | V | GVL_MODBUS.ADM100W_InputRegisters[5] | GVL_COM.COM_<INSTANCE>.COM_INPUT_IR[5] | Read, cyclic
IR | 6 | 6 | FC04 Read Input Registers | Equipment to PLC | ADM100W L1 Current | REAL | MSW | 1 | A | GVL_MODBUS.ADM100W_InputRegisters[6] | GVL_COM.COM_<INSTANCE>.COM_INPUT_IR[6] | Read, cyclic
IR | 7 | 7 | FC04 Read Input Registers | Equipment to PLC | ADM100W L1 Current | REAL | LSW | 1 | A | GVL_MODBUS.ADM100W_InputRegisters[7] | GVL_COM.COM_<INSTANCE>.COM_INPUT_IR[7] | Read, cyclic
IR | 8 | 8 | FC04 Read Input Registers | Equipment to PLC | ADM100W L1 Active Power | REAL | MSW | 1 | per ADM100W config | GVL_MODBUS.ADM100W_InputRegisters[8] | GVL_COM.COM_<INSTANCE>.COM_INPUT_IR[8] | Read, cyclic
IR | 9 | 9 | FC04 Read Input Registers | Equipment to PLC | ADM100W L1 Active Power | REAL | LSW | 1 | per ADM100W config | GVL_MODBUS.ADM100W_InputRegisters[9] | GVL_COM.COM_<INSTANCE>.COM_INPUT_IR[9] | Read, cyclic
IR | 10 | 10 | FC04 Read Input Registers | Equipment to PLC | ADM100W L1 Apparent Power | REAL | MSW | 1 | per ADM100W config | GVL_MODBUS.ADM100W_InputRegisters[10] | GVL_COM.COM_<INSTANCE>.COM_INPUT_IR[10] | Read, cyclic
IR | 11 | 11 | FC04 Read Input Registers | Equipment to PLC | ADM100W L1 Apparent Power | REAL | LSW | 1 | per ADM100W config | GVL_MODBUS.ADM100W_InputRegisters[11] | GVL_COM.COM_<INSTANCE>.COM_INPUT_IR[11] | Read, cyclic
IR | 12 | 12 | FC04 Read Input Registers | Equipment to PLC | ADM100W L1 Reactive Power | REAL | MSW | 1 | per ADM100W config | GVL_MODBUS.ADM100W_InputRegisters[12] | GVL_COM.COM_<INSTANCE>.COM_INPUT_IR[12] | Read, cyclic
IR | 13 | 13 | FC04 Read Input Registers | Equipment to PLC | ADM100W L1 Reactive Power | REAL | LSW | 1 | per ADM100W config | GVL_MODBUS.ADM100W_InputRegisters[13] | GVL_COM.COM_<INSTANCE>.COM_INPUT_IR[13] | Read, cyclic
IR | 14 | 14 | FC04 Read Input Registers | Equipment to PLC | ADM100W L1 Current Phase Angle | REAL | MSW | 1 | ° | GVL_MODBUS.ADM100W_InputRegisters[14] | GVL_COM.COM_<INSTANCE>.COM_INPUT_IR[14] | Read, cyclic
IR | 15 | 15 | FC04 Read Input Registers | Equipment to PLC | ADM100W L1 Current Phase Angle | REAL | LSW | 1 | ° | GVL_MODBUS.ADM100W_InputRegisters[15] | GVL_COM.COM_<INSTANCE>.COM_INPUT_IR[15] | Read, cyclic
IR | 16 | 16 | FC04 Read Input Registers | Equipment to PLC | ADM100W L1 Power Factor | REAL | MSW | 1 |  | GVL_MODBUS.ADM100W_InputRegisters[16] | GVL_COM.COM_<INSTANCE>.COM_INPUT_IR[16] | Read, cyclic
IR | 17 | 17 | FC04 Read Input Registers | Equipment to PLC | ADM100W L1 Power Factor | REAL | LSW | 1 |  | GVL_MODBUS.ADM100W_InputRegisters[17] | GVL_COM.COM_<INSTANCE>.COM_INPUT_IR[17] | Read, cyclic
IR | 18 | 18 | FC04 Read Input Registers | Equipment to PLC | ADM100W L1 Voltage THD | REAL | MSW | 1 | % | GVL_MODBUS.ADM100W_InputRegisters[18] | GVL_COM.COM_<INSTANCE>.COM_INPUT_IR[18] | Read, cyclic
IR | 19 | 19 | FC04 Read Input Registers | Equipment to PLC | ADM100W L1 Voltage THD | REAL | LSW | 1 | % | GVL_MODBUS.ADM100W_InputRegisters[19] | GVL_COM.COM_<INSTANCE>.COM_INPUT_IR[19] | Read, cyclic
IR | 20 | 20 | FC04 Read Input Registers | Equipment to PLC | ADM100W L1 Current THD | REAL | MSW | 1 | % | GVL_MODBUS.ADM100W_InputRegisters[20] | GVL_COM.COM_<INSTANCE>.COM_INPUT_IR[20] | Read, cyclic
IR | 21 | 21 | FC04 Read Input Registers | Equipment to PLC | ADM100W L1 Current THD | REAL | LSW | 1 | % | GVL_MODBUS.ADM100W_InputRegisters[21] | GVL_COM.COM_<INSTANCE>.COM_INPUT_IR[21] | Read, cyclic
IR | 22 | 22 | FC04 Read Input Registers | Equipment to PLC | ADM100W L1 Max Load | REAL | MSW | 1 | per ADM100W config | GVL_MODBUS.ADM100W_InputRegisters[22] | GVL_COM.COM_<INSTANCE>.COM_INPUT_IR[22] | Read, cyclic
IR | 23 | 23 | FC04 Read Input Registers | Equipment to PLC | ADM100W L1 Max Load | REAL | LSW | 1 | per ADM100W config | GVL_MODBUS.ADM100W_InputRegisters[23] | GVL_COM.COM_<INSTANCE>.COM_INPUT_IR[23] | Read, cyclic
IR | 24 | 24 | FC04 Read Input Registers | Equipment to PLC | ADM100W L1-L2 Voltage Phase Angle | REAL | MSW | 1 | ° | GVL_MODBUS.ADM100W_InputRegisters[24] | GVL_COM.COM_<INSTANCE>.COM_INPUT_IR[24] | Read, cyclic
IR | 25 | 25 | FC04 Read Input Registers | Equipment to PLC | ADM100W L1-L2 Voltage Phase Angle | REAL | LSW | 1 | ° | GVL_MODBUS.ADM100W_InputRegisters[25] | GVL_COM.COM_<INSTANCE>.COM_INPUT_IR[25] | Read, cyclic
IR | 26 | 26 | FC04 Read Input Registers | Equipment to PLC | ADM100W L2-L3 Voltage | REAL | MSW | 1 | V | GVL_MODBUS.ADM100W_InputRegisters[26] | GVL_COM.COM_<INSTANCE>.COM_INPUT_IR[26] | Read, cyclic
IR | 27 | 27 | FC04 Read Input Registers | Equipment to PLC | ADM100W L2-L3 Voltage | REAL | LSW | 1 | V | GVL_MODBUS.ADM100W_InputRegisters[27] | GVL_COM.COM_<INSTANCE>.COM_INPUT_IR[27] | Read, cyclic
IR | 28 | 28 | FC04 Read Input Registers | Equipment to PLC | ADM100W L2-N Voltage | REAL | MSW | 1 | V | GVL_MODBUS.ADM100W_InputRegisters[28] | GVL_COM.COM_<INSTANCE>.COM_INPUT_IR[28] | Read, cyclic
IR | 29 | 29 | FC04 Read Input Registers | Equipment to PLC | ADM100W L2-N Voltage | REAL | LSW | 1 | V | GVL_MODBUS.ADM100W_InputRegisters[29] | GVL_COM.COM_<INSTANCE>.COM_INPUT_IR[29] | Read, cyclic
IR | 30 | 30 | FC04 Read Input Registers | Equipment to PLC | ADM100W L2 Current | REAL | MSW | 1 | A | GVL_MODBUS.ADM100W_InputRegisters[30] | GVL_COM.COM_<INSTANCE>.COM_INPUT_IR[30] | Read, cyclic
IR | 31 | 31 | FC04 Read Input Registers | Equipment to PLC | ADM100W L2 Current | REAL | LSW | 1 | A | GVL_MODBUS.ADM100W_InputRegisters[31] | GVL_COM.COM_<INSTANCE>.COM_INPUT_IR[31] | Read, cyclic
IR | 32 | 32 | FC04 Read Input Registers | Equipment to PLC | ADM100W L2 Active Power | REAL | MSW | 1 | per ADM100W config | GVL_MODBUS.ADM100W_InputRegisters[32] | GVL_COM.COM_<INSTANCE>.COM_INPUT_IR[32] | Read, cyclic
IR | 33 | 33 | FC04 Read Input Registers | Equipment to PLC | ADM100W L2 Active Power | REAL | LSW | 1 | per ADM100W config | GVL_MODBUS.ADM100W_InputRegisters[33] | GVL_COM.COM_<INSTANCE>.COM_INPUT_IR[33] | Read, cyclic
IR | 34 | 34 | FC04 Read Input Registers | Equipment to PLC | ADM100W L2 Apparent Power | REAL | MSW | 1 | per ADM100W config | GVL_MODBUS.ADM100W_InputRegisters[34] | GVL_COM.COM_<INSTANCE>.COM_INPUT_IR[34] | Read, cyclic
IR | 35 | 35 | FC04 Read Input Registers | Equipment to PLC | ADM100W L2 Apparent Power | REAL | LSW | 1 | per ADM100W config | GVL_MODBUS.ADM100W_InputRegisters[35] | GVL_COM.COM_<INSTANCE>.COM_INPUT_IR[35] | Read, cyclic
IR | 36 | 36 | FC04 Read Input Registers | Equipment to PLC | ADM100W L2 Reactive Power | REAL | MSW | 1 | per ADM100W config | GVL_MODBUS.ADM100W_InputRegisters[36] | GVL_COM.COM_<INSTANCE>.COM_INPUT_IR[36] | Read, cyclic
IR | 37 | 37 | FC04 Read Input Registers | Equipment to PLC | ADM100W L2 Reactive Power | REAL | LSW | 1 | per ADM100W config | GVL_MODBUS.ADM100W_InputRegisters[37] | GVL_COM.COM_<INSTANCE>.COM_INPUT_IR[37] | Read, cyclic
IR | 38 | 38 | FC04 Read Input Registers | Equipment to PLC | ADM100W L2 Current Phase Angle | REAL | MSW | 1 | ° | GVL_MODBUS.ADM100W_InputRegisters[38] | GVL_COM.COM_<INSTANCE>.COM_INPUT_IR[38] | Read, cyclic
IR | 39 | 39 | FC04 Read Input Registers | Equipment to PLC | ADM100W L2 Current Phase Angle | REAL | LSW | 1 | ° | GVL_MODBUS.ADM100W_InputRegisters[39] | GVL_COM.COM_<INSTANCE>.COM_INPUT_IR[39] | Read, cyclic
IR | 40 | 40 | FC04 Read Input Registers | Equipment to PLC | ADM100W L2 Power Factor | REAL | MSW | 1 |  | GVL_MODBUS.ADM100W_InputRegisters[40] | GVL_COM.COM_<INSTANCE>.COM_INPUT_IR[40] | Read, cyclic
IR | 41 | 41 | FC04 Read Input Registers | Equipment to PLC | ADM100W L2 Power Factor | REAL | LSW | 1 |  | GVL_MODBUS.ADM100W_InputRegisters[41] | GVL_COM.COM_<INSTANCE>.COM_INPUT_IR[41] | Read, cyclic
IR | 42 | 42 | FC04 Read Input Registers | Equipment to PLC | ADM100W L2 Voltage THD | REAL | MSW | 1 | % | GVL_MODBUS.ADM100W_InputRegisters[42] | GVL_COM.COM_<INSTANCE>.COM_INPUT_IR[42] | Read, cyclic
IR | 43 | 43 | FC04 Read Input Registers | Equipment to PLC | ADM100W L2 Voltage THD | REAL | LSW | 1 | % | GVL_MODBUS.ADM100W_InputRegisters[43] | GVL_COM.COM_<INSTANCE>.COM_INPUT_IR[43] | Read, cyclic
IR | 44 | 44 | FC04 Read Input Registers | Equipment to PLC | ADM100W L2 Current THD | REAL | MSW | 1 | % | GVL_MODBUS.ADM100W_InputRegisters[44] | GVL_COM.COM_<INSTANCE>.COM_INPUT_IR[44] | Read, cyclic
IR | 45 | 45 | FC04 Read Input Registers | Equipment to PLC | ADM100W L2 Current THD | REAL | LSW | 1 | % | GVL_MODBUS.ADM100W_InputRegisters[45] | GVL_COM.COM_<INSTANCE>.COM_INPUT_IR[45] | Read, cyclic
IR | 46 | 46 | FC04 Read Input Registers | Equipment to PLC | ADM100W L2 Max Load | REAL | MSW | 1 | per ADM100W config | GVL_MODBUS.ADM100W_InputRegisters[46] | GVL_COM.COM_<INSTANCE>.COM_INPUT_IR[46] | Read, cyclic
IR | 47 | 47 | FC04 Read Input Registers | Equipment to PLC | ADM100W L2 Max Load | REAL | LSW | 1 | per ADM100W config | GVL_MODBUS.ADM100W_InputRegisters[47] | GVL_COM.COM_<INSTANCE>.COM_INPUT_IR[47] | Read, cyclic
IR | 48 | 48 | FC04 Read Input Registers | Equipment to PLC | ADM100W L1-L3 Voltage Phase Angle | REAL | MSW | 1 | ° | GVL_MODBUS.ADM100W_InputRegisters[48] | GVL_COM.COM_<INSTANCE>.COM_INPUT_IR[48] | Read, cyclic
IR | 49 | 49 | FC04 Read Input Registers | Equipment to PLC | ADM100W L1-L3 Voltage Phase Angle | REAL | LSW | 1 | ° | GVL_MODBUS.ADM100W_InputRegisters[49] | GVL_COM.COM_<INSTANCE>.COM_INPUT_IR[49] | Read, cyclic
IR | 50 | 50 | FC04 Read Input Registers | Equipment to PLC | ADM100W L3-L1 Voltage | REAL | MSW | 1 | V | GVL_MODBUS.ADM100W_InputRegisters[50] | GVL_COM.COM_<INSTANCE>.COM_INPUT_IR[50] | Read, cyclic
IR | 51 | 51 | FC04 Read Input Registers | Equipment to PLC | ADM100W L3-L1 Voltage | REAL | LSW | 1 | V | GVL_MODBUS.ADM100W_InputRegisters[51] | GVL_COM.COM_<INSTANCE>.COM_INPUT_IR[51] | Read, cyclic
IR | 52 | 52 | FC04 Read Input Registers | Equipment to PLC | ADM100W L3-N Voltage | REAL | MSW | 1 | V | GVL_MODBUS.ADM100W_InputRegisters[52] | GVL_COM.COM_<INSTANCE>.COM_INPUT_IR[52] | Read, cyclic
IR | 53 | 53 | FC04 Read Input Registers | Equipment to PLC | ADM100W L3-N Voltage | REAL | LSW | 1 | V | GVL_MODBUS.ADM100W_InputRegisters[53] | GVL_COM.COM_<INSTANCE>.COM_INPUT_IR[53] | Read, cyclic
IR | 54 | 54 | FC04 Read Input Registers | Equipment to PLC | ADM100W L3 Current | REAL | MSW | 1 | A | GVL_MODBUS.ADM100W_InputRegisters[54] | GVL_COM.COM_<INSTANCE>.COM_INPUT_IR[54] | Read, cyclic
IR | 55 | 55 | FC04 Read Input Registers | Equipment to PLC | ADM100W L3 Current | REAL | LSW | 1 | A | GVL_MODBUS.ADM100W_InputRegisters[55] | GVL_COM.COM_<INSTANCE>.COM_INPUT_IR[55] | Read, cyclic
IR | 56 | 56 | FC04 Read Input Registers | Equipment to PLC | ADM100W L3 Active Power | REAL | MSW | 1 | per ADM100W config | GVL_MODBUS.ADM100W_InputRegisters[56] | GVL_COM.COM_<INSTANCE>.COM_INPUT_IR[56] | Read, cyclic
IR | 57 | 57 | FC04 Read Input Registers | Equipment to PLC | ADM100W L3 Active Power | REAL | LSW | 1 | per ADM100W config | GVL_MODBUS.ADM100W_InputRegisters[57] | GVL_COM.COM_<INSTANCE>.COM_INPUT_IR[57] | Read, cyclic
IR | 58 | 58 | FC04 Read Input Registers | Equipment to PLC | ADM100W L3 Apparent Power | REAL | MSW | 1 | per ADM100W config | GVL_MODBUS.ADM100W_InputRegisters[58] | GVL_COM.COM_<INSTANCE>.COM_INPUT_IR[58] | Read, cyclic
IR | 59 | 59 | FC04 Read Input Registers | Equipment to PLC | ADM100W L3 Apparent Power | REAL | LSW | 1 | per ADM100W config | GVL_MODBUS.ADM100W_InputRegisters[59] | GVL_COM.COM_<INSTANCE>.COM_INPUT_IR[59] | Read, cyclic
IR | 60 | 60 | FC04 Read Input Registers | Equipment to PLC | ADM100W L3 Reactive Power | REAL | MSW | 1 | per ADM100W config | GVL_MODBUS.ADM100W_InputRegisters[60] | GVL_COM.COM_<INSTANCE>.COM_INPUT_IR[60] | Read, cyclic
IR | 61 | 61 | FC04 Read Input Registers | Equipment to PLC | ADM100W L3 Reactive Power | REAL | LSW | 1 | per ADM100W config | GVL_MODBUS.ADM100W_InputRegisters[61] | GVL_COM.COM_<INSTANCE>.COM_INPUT_IR[61] | Read, cyclic
IR | 62 | 62 | FC04 Read Input Registers | Equipment to PLC | ADM100W L3 Current Phase Angle | REAL | MSW | 1 | ° | GVL_MODBUS.ADM100W_InputRegisters[62] | GVL_COM.COM_<INSTANCE>.COM_INPUT_IR[62] | Read, cyclic
IR | 63 | 63 | FC04 Read Input Registers | Equipment to PLC | ADM100W L3 Current Phase Angle | REAL | LSW | 1 | ° | GVL_MODBUS.ADM100W_InputRegisters[63] | GVL_COM.COM_<INSTANCE>.COM_INPUT_IR[63] | Read, cyclic
IR | 64 | 64 | FC04 Read Input Registers | Equipment to PLC | ADM100W L3 Power Factor | REAL | MSW | 1 |  | GVL_MODBUS.ADM100W_InputRegisters[64] | GVL_COM.COM_<INSTANCE>.COM_INPUT_IR[64] | Read, cyclic
IR | 65 | 65 | FC04 Read Input Registers | Equipment to PLC | ADM100W L3 Power Factor | REAL | LSW | 1 |  | GVL_MODBUS.ADM100W_InputRegisters[65] | GVL_COM.COM_<INSTANCE>.COM_INPUT_IR[65] | Read, cyclic
IR | 66 | 66 | FC04 Read Input Registers | Equipment to PLC | ADM100W L3 Voltage THD | REAL | MSW | 1 | % | GVL_MODBUS.ADM100W_InputRegisters[66] | GVL_COM.COM_<INSTANCE>.COM_INPUT_IR[66] | Read, cyclic
IR | 67 | 67 | FC04 Read Input Registers | Equipment to PLC | ADM100W L3 Voltage THD | REAL | LSW | 1 | % | GVL_MODBUS.ADM100W_InputRegisters[67] | GVL_COM.COM_<INSTANCE>.COM_INPUT_IR[67] | Read, cyclic
IR | 68 | 68 | FC04 Read Input Registers | Equipment to PLC | ADM100W L3 Current THD | REAL | MSW | 1 | % | GVL_MODBUS.ADM100W_InputRegisters[68] | GVL_COM.COM_<INSTANCE>.COM_INPUT_IR[68] | Read, cyclic
IR | 69 | 69 | FC04 Read Input Registers | Equipment to PLC | ADM100W L3 Current THD | REAL | LSW | 1 | % | GVL_MODBUS.ADM100W_InputRegisters[69] | GVL_COM.COM_<INSTANCE>.COM_INPUT_IR[69] | Read, cyclic
IR | 70 | 70 | FC04 Read Input Registers | Equipment to PLC | ADM100W L3 Max Load | REAL | MSW | 1 | per ADM100W config | GVL_MODBUS.ADM100W_InputRegisters[70] | GVL_COM.COM_<INSTANCE>.COM_INPUT_IR[70] | Read, cyclic
IR | 71 | 71 | FC04 Read Input Registers | Equipment to PLC | ADM100W L3 Max Load | REAL | LSW | 1 | per ADM100W config | GVL_MODBUS.ADM100W_InputRegisters[71] | GVL_COM.COM_<INSTANCE>.COM_INPUT_IR[71] | Read, cyclic
IR | 72 | 72 | FC04 Read Input Registers | Equipment to PLC | ADM100W Internal Temperature | REAL | MSW | 1 | per ADM100W config | GVL_MODBUS.ADM100W_InputRegisters[72] | GVL_COM.COM_<INSTANCE>.COM_INPUT_IR[72] | Read, cyclic
IR | 73 | 73 | FC04 Read Input Registers | Equipment to PLC | ADM100W Internal Temperature | REAL | LSW | 1 | per ADM100W config | GVL_MODBUS.ADM100W_InputRegisters[73] | GVL_COM.COM_<INSTANCE>.COM_INPUT_IR[73] | Read, cyclic
IR | 74 | 74 | FC04 Read Input Registers | Equipment to PLC | ADM100W Active Energy | REAL | MSW | 1 | per ADM100W config | GVL_MODBUS.ADM100W_InputRegisters[74] | GVL_COM.COM_<INSTANCE>.COM_INPUT_IR[74] | Read, cyclic
IR | 75 | 75 | FC04 Read Input Registers | Equipment to PLC | ADM100W Active Energy | REAL | LSW | 1 | per ADM100W config | GVL_MODBUS.ADM100W_InputRegisters[75] | GVL_COM.COM_<INSTANCE>.COM_INPUT_IR[75] | Read, cyclic
IR | 76 | 76 | FC04 Read Input Registers | Equipment to PLC | ADM100W Apparent Energy | REAL | MSW | 1 | per ADM100W config | GVL_MODBUS.ADM100W_InputRegisters[76] | GVL_COM.COM_<INSTANCE>.COM_INPUT_IR[76] | Read, cyclic
IR | 77 | 77 | FC04 Read Input Registers | Equipment to PLC | ADM100W Apparent Energy | REAL | LSW | 1 | per ADM100W config | GVL_MODBUS.ADM100W_InputRegisters[77] | GVL_COM.COM_<INSTANCE>.COM_INPUT_IR[77] | Read, cyclic
IR | 78 | 78 | FC04 Read Input Registers | Equipment to PLC | ADM100W Reactive Energy | REAL | MSW | 1 | per ADM100W config | GVL_MODBUS.ADM100W_InputRegisters[78] | GVL_COM.COM_<INSTANCE>.COM_INPUT_IR[78] | Read, cyclic
IR | 79 | 79 | FC04 Read Input Registers | Equipment to PLC | ADM100W Reactive Energy | REAL | LSW | 1 | per ADM100W config | GVL_MODBUS.ADM100W_InputRegisters[79] | GVL_COM.COM_<INSTANCE>.COM_INPUT_IR[79] | Read, cyclic
IR | 80 | 80 | FC04 Read Input Registers | Equipment to PLC | ADM100W Total Active Power | REAL | MSW | 1 | per ADM100W config | GVL_MODBUS.ADM100W_InputRegisters[80] | GVL_COM.COM_<INSTANCE>.COM_INPUT_IR[80] | Read, cyclic
IR | 81 | 81 | FC04 Read Input Registers | Equipment to PLC | ADM100W Total Active Power | REAL | LSW | 1 | per ADM100W config | GVL_MODBUS.ADM100W_InputRegisters[81] | GVL_COM.COM_<INSTANCE>.COM_INPUT_IR[81] | Read, cyclic
IR | 82 | 82 | FC04 Read Input Registers | Equipment to PLC | ADM100W Total Apparent Power | REAL | MSW | 1 | per ADM100W config | GVL_MODBUS.ADM100W_InputRegisters[82] | GVL_COM.COM_<INSTANCE>.COM_INPUT_IR[82] | Read, cyclic
IR | 83 | 83 | FC04 Read Input Registers | Equipment to PLC | ADM100W Total Apparent Power | REAL | LSW | 1 | per ADM100W config | GVL_MODBUS.ADM100W_InputRegisters[83] | GVL_COM.COM_<INSTANCE>.COM_INPUT_IR[83] | Read, cyclic
IR | 84 | 84 | FC04 Read Input Registers | Equipment to PLC | ADM100W Total Reactive Power | REAL | MSW | 1 | per ADM100W config | GVL_MODBUS.ADM100W_InputRegisters[84] | GVL_COM.COM_<INSTANCE>.COM_INPUT_IR[84] | Read, cyclic
IR | 85 | 85 | FC04 Read Input Registers | Equipment to PLC | ADM100W Total Reactive Power | REAL | LSW | 1 | per ADM100W config | GVL_MODBUS.ADM100W_InputRegisters[85] | GVL_COM.COM_<INSTANCE>.COM_INPUT_IR[85] | Read, cyclic
IR | 86 | 86 | FC04 Read Input Registers | Equipment to PLC | ADM100W All Phase Power Factor | REAL | MSW | 1 |  | GVL_MODBUS.ADM100W_InputRegisters[86] | GVL_COM.COM_<INSTANCE>.COM_INPUT_IR[86] | Read, cyclic
IR | 87 | 87 | FC04 Read Input Registers | Equipment to PLC | ADM100W All Phase Power Factor | REAL | LSW | 1 |  | GVL_MODBUS.ADM100W_InputRegisters[87] | GVL_COM.COM_<INSTANCE>.COM_INPUT_IR[87] | Read, cyclic
Note on A1: Modbus table : Coil, DI (discrete input), IR (input register), HR (holding register).
Note on B1: Register or coil address as written in the equipment manual (hex 0x4001 or decimal).
Note on C1: Position in the CODESYS Modbus channel and in the GVL_MODBUS array (0 = first register of the channel).
Note on D1: Modbus function code used by the CODESYS channel.
Note on E1: Equipment to PLC = read by the PLC. PLC to Equipment = written by the PLC.
Note on F1: Readable name of the value. Used as tag name in FUXA and as label in the supervisions.
Note on G1: Type of the value in the equipment. 32-bit values use 2 rows.
Note on H1: 32-bit value split in 2 registers : MSW = most significant word, LSW = least significant word. Empty for 16-bit and BOOL.
Note on I1: Conversion raw value -> engineering value, as written in the equipment manual. "1" = no conversion.
Note on J1: Engineering unit of the value (free text).
Note on K1: Element of GVL_MODBUS mapped in the CODESYS device I/O mapping (Modbus server or slave channel). GVL_MODBUS = exchange variables only.
Note on L1: Variable of GVL_COM copied to / from GVL_MODBUS by GFC_COM_IN / GFC_COM_OUT.
Note on M1: How the CODESYS Modbus master channel runs : cyclic, or on the rising edge of a trigger variable mapped in the slave I/O mapping.
Note on N1: Free text. Not used by the generator.

## TEMPLATE_EXC
FC | Instance A | Instance B | Parameter A value | Parameter B value | Comment
FC_EXC_UPI_LOCAL_FUXA_ADM100W | UPI_LOCAL_FUXA | <INSTANCE> | GVL_EXC.EXC_UPI_LOCAL_FUXA | GVL_EXC.EXC_<INSTANCE>
FC_EXC_UPI_LOCAL_HMI_ADM100W | UPI_LOCAL_HMI | <INSTANCE> | GVL_EXC.EXC_UPI_LOCAL_HMI | GVL_EXC.EXC_<INSTANCE>
FC_EXC_UPI_LOCAL_WEBVISU_ADM100W | UPI_LOCAL_WEBVISU | <INSTANCE> | GVL_EXC.EXC_UPI_LOCAL_WEBVISU | GVL_EXC.EXC_<INSTANCE>
Note on A1: Exchange function FC_EXC_<type A>_<type B> (folder Functions / FC_EXC). Same FC for every instance pair of these two types.
Note on B1: Instance given to parameter A in the GFC_EXC call.
Note on C1: Instance given to parameter B in the GFC_EXC call.
Note on D1: Variable given to parameter A in the GFC_EXC call : GVL_EXC.EXC_<instance A>.
Note on E1: Variable given to parameter B in the GFC_EXC call : GVL_EXC.EXC_<instance B>.
Note on F1: Comment of the destination member in its DUT_EXC.

## TEMPLATE_TCP
Modbus address | Client address | Client | Instance | Name | Direction | Type | Word | Scale | Unit | GVL_MODBUS variable | GVL_COM variable | Comment
|  | HMI | <INSTANCE> | ADM100W Local Request | Client to PLC | BOOL |  |  |  |  | GVL_COM.COM_<INSTANCE>.HMI_INPUT_LOCAL_REQUEST | Paste in COILS
|  | HMI | <INSTANCE> | ADM100W Auto Request | Client to PLC | BOOL |  |  |  |  | GVL_COM.COM_<INSTANCE>.HMI_INPUT_AUTO_REQUEST | Paste in COILS
|  | FUXA | <INSTANCE> | ADM100W Local Request | Client to PLC | BOOL |  |  |  |  | GVL_COM.COM_<INSTANCE>.SCADA_INPUT_LOCAL_REQUEST | Paste in COILS
|  | FUXA | <INSTANCE> | ADM100W Auto Request | Client to PLC | BOOL |  |  |  |  | GVL_COM.COM_<INSTANCE>.SCADA_INPUT_AUTO_REQUEST | Paste in COILS
|  | HMI | <INSTANCE> | ADM100W Alarm 1 Status | PLC to Client | BOOL |  |  |  |  | GVL_COM.COM_<INSTANCE>.HMI_OUTPUT_ALARM_1_STATUS | Paste in DISCRETE_INPUTS
|  | HMI | <INSTANCE> | ADM100W Alarm 2 Status | PLC to Client | BOOL |  |  |  |  | GVL_COM.COM_<INSTANCE>.HMI_OUTPUT_ALARM_2_STATUS | Paste in DISCRETE_INPUTS
|  | HMI | <INSTANCE> | ADM100W Alarm 3 Status | PLC to Client | BOOL |  |  |  |  | GVL_COM.COM_<INSTANCE>.HMI_OUTPUT_ALARM_3_STATUS | Paste in DISCRETE_INPUTS
|  | HMI | <INSTANCE> | ADM100W Alarm 4 Status | PLC to Client | BOOL |  |  |  |  | GVL_COM.COM_<INSTANCE>.HMI_OUTPUT_ALARM_4_STATUS | Paste in DISCRETE_INPUTS
|  | HMI | <INSTANCE> | ADM100W Alarm 5 Status | PLC to Client | BOOL |  |  |  |  | GVL_COM.COM_<INSTANCE>.HMI_OUTPUT_ALARM_5_STATUS | Paste in DISCRETE_INPUTS
|  | HMI | <INSTANCE> | ADM100W Alarm 6 Status | PLC to Client | BOOL |  |  |  |  | GVL_COM.COM_<INSTANCE>.HMI_OUTPUT_ALARM_6_STATUS | Paste in DISCRETE_INPUTS
|  | HMI | <INSTANCE> | ADM100W Alarm 7 Status | PLC to Client | BOOL |  |  |  |  | GVL_COM.COM_<INSTANCE>.HMI_OUTPUT_ALARM_7_STATUS | Paste in DISCRETE_INPUTS
|  | HMI | <INSTANCE> | ADM100W Alarm 8 Status | PLC to Client | BOOL |  |  |  |  | GVL_COM.COM_<INSTANCE>.HMI_OUTPUT_ALARM_8_STATUS | Paste in DISCRETE_INPUTS
|  | HMI | <INSTANCE> | ADM100W Alarm 9 Status | PLC to Client | BOOL |  |  |  |  | GVL_COM.COM_<INSTANCE>.HMI_OUTPUT_ALARM_9_STATUS | Paste in DISCRETE_INPUTS
|  | HMI | <INSTANCE> | ADM100W Alarm 10 Status | PLC to Client | BOOL |  |  |  |  | GVL_COM.COM_<INSTANCE>.HMI_OUTPUT_ALARM_10_STATUS | Paste in DISCRETE_INPUTS
|  | HMI | <INSTANCE> | ADM100W Local Active | PLC to Client | BOOL |  |  |  |  | GVL_COM.COM_<INSTANCE>.HMI_OUTPUT_LOCAL_ACTIVE | Paste in DISCRETE_INPUTS
|  | FUXA | <INSTANCE> | ADM100W Alarm 1 Status | PLC to Client | BOOL |  |  |  |  | GVL_COM.COM_<INSTANCE>.SCADA_OUTPUT_ALARM_1_STATUS | Paste in DISCRETE_INPUTS
|  | FUXA | <INSTANCE> | ADM100W Alarm 2 Status | PLC to Client | BOOL |  |  |  |  | GVL_COM.COM_<INSTANCE>.SCADA_OUTPUT_ALARM_2_STATUS | Paste in DISCRETE_INPUTS
|  | FUXA | <INSTANCE> | ADM100W Alarm 3 Status | PLC to Client | BOOL |  |  |  |  | GVL_COM.COM_<INSTANCE>.SCADA_OUTPUT_ALARM_3_STATUS | Paste in DISCRETE_INPUTS
|  | FUXA | <INSTANCE> | ADM100W Alarm 4 Status | PLC to Client | BOOL |  |  |  |  | GVL_COM.COM_<INSTANCE>.SCADA_OUTPUT_ALARM_4_STATUS | Paste in DISCRETE_INPUTS
|  | FUXA | <INSTANCE> | ADM100W Alarm 5 Status | PLC to Client | BOOL |  |  |  |  | GVL_COM.COM_<INSTANCE>.SCADA_OUTPUT_ALARM_5_STATUS | Paste in DISCRETE_INPUTS
|  | FUXA | <INSTANCE> | ADM100W Alarm 6 Status | PLC to Client | BOOL |  |  |  |  | GVL_COM.COM_<INSTANCE>.SCADA_OUTPUT_ALARM_6_STATUS | Paste in DISCRETE_INPUTS
|  | FUXA | <INSTANCE> | ADM100W Alarm 7 Status | PLC to Client | BOOL |  |  |  |  | GVL_COM.COM_<INSTANCE>.SCADA_OUTPUT_ALARM_7_STATUS | Paste in DISCRETE_INPUTS
|  | FUXA | <INSTANCE> | ADM100W Alarm 8 Status | PLC to Client | BOOL |  |  |  |  | GVL_COM.COM_<INSTANCE>.SCADA_OUTPUT_ALARM_8_STATUS | Paste in DISCRETE_INPUTS
|  | FUXA | <INSTANCE> | ADM100W Alarm 9 Status | PLC to Client | BOOL |  |  |  |  | GVL_COM.COM_<INSTANCE>.SCADA_OUTPUT_ALARM_9_STATUS | Paste in DISCRETE_INPUTS
|  | FUXA | <INSTANCE> | ADM100W Alarm 10 Status | PLC to Client | BOOL |  |  |  |  | GVL_COM.COM_<INSTANCE>.SCADA_OUTPUT_ALARM_10_STATUS | Paste in DISCRETE_INPUTS
|  | FUXA | <INSTANCE> | ADM100W Local FUXA Active | PLC to Client | BOOL |  |  |  |  | GVL_COM.COM_<INSTANCE>.SCADA_OUTPUT_LOCAL_FUXA_ACTIVE | Paste in DISCRETE_INPUTS
|  | FUXA | <INSTANCE> | ADM100W Local HMI Active | PLC to Client | BOOL |  |  |  |  | GVL_COM.COM_<INSTANCE>.SCADA_OUTPUT_LOCAL_HMI_ACTIVE | Paste in DISCRETE_INPUTS
|  | HMI | <INSTANCE> | ADM100W Frequency | PLC to Client | REAL | LSW | 1 | Hz |  | GVL_COM.COM_<INSTANCE>.HMI_OUTPUT_FREQUENCY.Word_value[0] | Paste in INPUT_REGISTERS
|  | HMI | <INSTANCE> | ADM100W Frequency | PLC to Client | REAL | MSW | 1 | Hz |  | GVL_COM.COM_<INSTANCE>.HMI_OUTPUT_FREQUENCY.Word_value[1] | Paste in INPUT_REGISTERS
|  | HMI | <INSTANCE> | ADM100W L1-L2 Voltage | PLC to Client | REAL | LSW | 1 | V |  | GVL_COM.COM_<INSTANCE>.HMI_OUTPUT_L1_L2_VOLTAGE.Word_value[0] | Paste in INPUT_REGISTERS
|  | HMI | <INSTANCE> | ADM100W L1-L2 Voltage | PLC to Client | REAL | MSW | 1 | V |  | GVL_COM.COM_<INSTANCE>.HMI_OUTPUT_L1_L2_VOLTAGE.Word_value[1] | Paste in INPUT_REGISTERS
|  | HMI | <INSTANCE> | ADM100W L1-N Voltage | PLC to Client | REAL | LSW | 1 | V |  | GVL_COM.COM_<INSTANCE>.HMI_OUTPUT_L1_N_VOLTAGE.Word_value[0] | Paste in INPUT_REGISTERS
|  | HMI | <INSTANCE> | ADM100W L1-N Voltage | PLC to Client | REAL | MSW | 1 | V |  | GVL_COM.COM_<INSTANCE>.HMI_OUTPUT_L1_N_VOLTAGE.Word_value[1] | Paste in INPUT_REGISTERS
|  | HMI | <INSTANCE> | ADM100W L1 Current | PLC to Client | REAL | LSW | 1 | A |  | GVL_COM.COM_<INSTANCE>.HMI_OUTPUT_L1_CURRENT.Word_value[0] | Paste in INPUT_REGISTERS
|  | HMI | <INSTANCE> | ADM100W L1 Current | PLC to Client | REAL | MSW | 1 | A |  | GVL_COM.COM_<INSTANCE>.HMI_OUTPUT_L1_CURRENT.Word_value[1] | Paste in INPUT_REGISTERS
|  | HMI | <INSTANCE> | ADM100W L1 Active Power | PLC to Client | REAL | LSW | 1 | per ADM100W config |  | GVL_COM.COM_<INSTANCE>.HMI_OUTPUT_L1_ACTIVE_POWER.Word_value[0] | Paste in INPUT_REGISTERS
|  | HMI | <INSTANCE> | ADM100W L1 Active Power | PLC to Client | REAL | MSW | 1 | per ADM100W config |  | GVL_COM.COM_<INSTANCE>.HMI_OUTPUT_L1_ACTIVE_POWER.Word_value[1] | Paste in INPUT_REGISTERS
|  | HMI | <INSTANCE> | ADM100W L1 Apparent Power | PLC to Client | REAL | LSW | 1 | per ADM100W config |  | GVL_COM.COM_<INSTANCE>.HMI_OUTPUT_L1_APPARENT_POWER.Word_value[0] | Paste in INPUT_REGISTERS
|  | HMI | <INSTANCE> | ADM100W L1 Apparent Power | PLC to Client | REAL | MSW | 1 | per ADM100W config |  | GVL_COM.COM_<INSTANCE>.HMI_OUTPUT_L1_APPARENT_POWER.Word_value[1] | Paste in INPUT_REGISTERS
|  | HMI | <INSTANCE> | ADM100W L1 Reactive Power | PLC to Client | REAL | LSW | 1 | per ADM100W config |  | GVL_COM.COM_<INSTANCE>.HMI_OUTPUT_L1_REACTIVE_POWER.Word_value[0] | Paste in INPUT_REGISTERS
|  | HMI | <INSTANCE> | ADM100W L1 Reactive Power | PLC to Client | REAL | MSW | 1 | per ADM100W config |  | GVL_COM.COM_<INSTANCE>.HMI_OUTPUT_L1_REACTIVE_POWER.Word_value[1] | Paste in INPUT_REGISTERS
|  | HMI | <INSTANCE> | ADM100W L1 Current Phase Angle | PLC to Client | REAL | LSW | 1 | ° |  | GVL_COM.COM_<INSTANCE>.HMI_OUTPUT_L1_CURRENT_PHASE_ANGLE.Word_value[0] | Paste in INPUT_REGISTERS
|  | HMI | <INSTANCE> | ADM100W L1 Current Phase Angle | PLC to Client | REAL | MSW | 1 | ° |  | GVL_COM.COM_<INSTANCE>.HMI_OUTPUT_L1_CURRENT_PHASE_ANGLE.Word_value[1] | Paste in INPUT_REGISTERS
|  | HMI | <INSTANCE> | ADM100W L1 Power Factor | PLC to Client | REAL | LSW | 1 |  |  | GVL_COM.COM_<INSTANCE>.HMI_OUTPUT_L1_POWER_FACTOR.Word_value[0] | Paste in INPUT_REGISTERS
|  | HMI | <INSTANCE> | ADM100W L1 Power Factor | PLC to Client | REAL | MSW | 1 |  |  | GVL_COM.COM_<INSTANCE>.HMI_OUTPUT_L1_POWER_FACTOR.Word_value[1] | Paste in INPUT_REGISTERS
|  | HMI | <INSTANCE> | ADM100W L1 Voltage THD | PLC to Client | REAL | LSW | 1 | % |  | GVL_COM.COM_<INSTANCE>.HMI_OUTPUT_L1_VOLTAGE_THD.Word_value[0] | Paste in INPUT_REGISTERS
|  | HMI | <INSTANCE> | ADM100W L1 Voltage THD | PLC to Client | REAL | MSW | 1 | % |  | GVL_COM.COM_<INSTANCE>.HMI_OUTPUT_L1_VOLTAGE_THD.Word_value[1] | Paste in INPUT_REGISTERS
|  | HMI | <INSTANCE> | ADM100W L1 Current THD | PLC to Client | REAL | LSW | 1 | % |  | GVL_COM.COM_<INSTANCE>.HMI_OUTPUT_L1_CURRENT_THD.Word_value[0] | Paste in INPUT_REGISTERS
|  | HMI | <INSTANCE> | ADM100W L1 Current THD | PLC to Client | REAL | MSW | 1 | % |  | GVL_COM.COM_<INSTANCE>.HMI_OUTPUT_L1_CURRENT_THD.Word_value[1] | Paste in INPUT_REGISTERS
|  | HMI | <INSTANCE> | ADM100W L1 Max Load | PLC to Client | REAL | LSW | 1 | per ADM100W config |  | GVL_COM.COM_<INSTANCE>.HMI_OUTPUT_L1_MAX_LOAD.Word_value[0] | Paste in INPUT_REGISTERS
|  | HMI | <INSTANCE> | ADM100W L1 Max Load | PLC to Client | REAL | MSW | 1 | per ADM100W config |  | GVL_COM.COM_<INSTANCE>.HMI_OUTPUT_L1_MAX_LOAD.Word_value[1] | Paste in INPUT_REGISTERS
|  | HMI | <INSTANCE> | ADM100W L1-L2 Voltage Phase Angle | PLC to Client | REAL | LSW | 1 | ° |  | GVL_COM.COM_<INSTANCE>.HMI_OUTPUT_L1_L2_VOLTAGE_PHASE_ANGLE.Word_value[0] | Paste in INPUT_REGISTERS
|  | HMI | <INSTANCE> | ADM100W L1-L2 Voltage Phase Angle | PLC to Client | REAL | MSW | 1 | ° |  | GVL_COM.COM_<INSTANCE>.HMI_OUTPUT_L1_L2_VOLTAGE_PHASE_ANGLE.Word_value[1] | Paste in INPUT_REGISTERS
|  | HMI | <INSTANCE> | ADM100W L2-L3 Voltage | PLC to Client | REAL | LSW | 1 | V |  | GVL_COM.COM_<INSTANCE>.HMI_OUTPUT_L2_L3_VOLTAGE.Word_value[0] | Paste in INPUT_REGISTERS
|  | HMI | <INSTANCE> | ADM100W L2-L3 Voltage | PLC to Client | REAL | MSW | 1 | V |  | GVL_COM.COM_<INSTANCE>.HMI_OUTPUT_L2_L3_VOLTAGE.Word_value[1] | Paste in INPUT_REGISTERS
|  | HMI | <INSTANCE> | ADM100W L2-N Voltage | PLC to Client | REAL | LSW | 1 | V |  | GVL_COM.COM_<INSTANCE>.HMI_OUTPUT_L2_N_VOLTAGE.Word_value[0] | Paste in INPUT_REGISTERS
|  | HMI | <INSTANCE> | ADM100W L2-N Voltage | PLC to Client | REAL | MSW | 1 | V |  | GVL_COM.COM_<INSTANCE>.HMI_OUTPUT_L2_N_VOLTAGE.Word_value[1] | Paste in INPUT_REGISTERS
|  | HMI | <INSTANCE> | ADM100W L2 Current | PLC to Client | REAL | LSW | 1 | A |  | GVL_COM.COM_<INSTANCE>.HMI_OUTPUT_L2_CURRENT.Word_value[0] | Paste in INPUT_REGISTERS
|  | HMI | <INSTANCE> | ADM100W L2 Current | PLC to Client | REAL | MSW | 1 | A |  | GVL_COM.COM_<INSTANCE>.HMI_OUTPUT_L2_CURRENT.Word_value[1] | Paste in INPUT_REGISTERS
|  | HMI | <INSTANCE> | ADM100W L2 Active Power | PLC to Client | REAL | LSW | 1 | per ADM100W config |  | GVL_COM.COM_<INSTANCE>.HMI_OUTPUT_L2_ACTIVE_POWER.Word_value[0] | Paste in INPUT_REGISTERS
|  | HMI | <INSTANCE> | ADM100W L2 Active Power | PLC to Client | REAL | MSW | 1 | per ADM100W config |  | GVL_COM.COM_<INSTANCE>.HMI_OUTPUT_L2_ACTIVE_POWER.Word_value[1] | Paste in INPUT_REGISTERS
|  | HMI | <INSTANCE> | ADM100W L2 Apparent Power | PLC to Client | REAL | LSW | 1 | per ADM100W config |  | GVL_COM.COM_<INSTANCE>.HMI_OUTPUT_L2_APPARENT_POWER.Word_value[0] | Paste in INPUT_REGISTERS
|  | HMI | <INSTANCE> | ADM100W L2 Apparent Power | PLC to Client | REAL | MSW | 1 | per ADM100W config |  | GVL_COM.COM_<INSTANCE>.HMI_OUTPUT_L2_APPARENT_POWER.Word_value[1] | Paste in INPUT_REGISTERS
|  | HMI | <INSTANCE> | ADM100W L2 Reactive Power | PLC to Client | REAL | LSW | 1 | per ADM100W config |  | GVL_COM.COM_<INSTANCE>.HMI_OUTPUT_L2_REACTIVE_POWER.Word_value[0] | Paste in INPUT_REGISTERS
|  | HMI | <INSTANCE> | ADM100W L2 Reactive Power | PLC to Client | REAL | MSW | 1 | per ADM100W config |  | GVL_COM.COM_<INSTANCE>.HMI_OUTPUT_L2_REACTIVE_POWER.Word_value[1] | Paste in INPUT_REGISTERS
|  | HMI | <INSTANCE> | ADM100W L2 Current Phase Angle | PLC to Client | REAL | LSW | 1 | ° |  | GVL_COM.COM_<INSTANCE>.HMI_OUTPUT_L2_CURRENT_PHASE_ANGLE.Word_value[0] | Paste in INPUT_REGISTERS
|  | HMI | <INSTANCE> | ADM100W L2 Current Phase Angle | PLC to Client | REAL | MSW | 1 | ° |  | GVL_COM.COM_<INSTANCE>.HMI_OUTPUT_L2_CURRENT_PHASE_ANGLE.Word_value[1] | Paste in INPUT_REGISTERS
|  | HMI | <INSTANCE> | ADM100W L2 Power Factor | PLC to Client | REAL | LSW | 1 |  |  | GVL_COM.COM_<INSTANCE>.HMI_OUTPUT_L2_POWER_FACTOR.Word_value[0] | Paste in INPUT_REGISTERS
|  | HMI | <INSTANCE> | ADM100W L2 Power Factor | PLC to Client | REAL | MSW | 1 |  |  | GVL_COM.COM_<INSTANCE>.HMI_OUTPUT_L2_POWER_FACTOR.Word_value[1] | Paste in INPUT_REGISTERS
|  | HMI | <INSTANCE> | ADM100W L2 Voltage THD | PLC to Client | REAL | LSW | 1 | % |  | GVL_COM.COM_<INSTANCE>.HMI_OUTPUT_L2_VOLTAGE_THD.Word_value[0] | Paste in INPUT_REGISTERS
|  | HMI | <INSTANCE> | ADM100W L2 Voltage THD | PLC to Client | REAL | MSW | 1 | % |  | GVL_COM.COM_<INSTANCE>.HMI_OUTPUT_L2_VOLTAGE_THD.Word_value[1] | Paste in INPUT_REGISTERS
|  | HMI | <INSTANCE> | ADM100W L2 Current THD | PLC to Client | REAL | LSW | 1 | % |  | GVL_COM.COM_<INSTANCE>.HMI_OUTPUT_L2_CURRENT_THD.Word_value[0] | Paste in INPUT_REGISTERS
|  | HMI | <INSTANCE> | ADM100W L2 Current THD | PLC to Client | REAL | MSW | 1 | % |  | GVL_COM.COM_<INSTANCE>.HMI_OUTPUT_L2_CURRENT_THD.Word_value[1] | Paste in INPUT_REGISTERS
|  | HMI | <INSTANCE> | ADM100W L2 Max Load | PLC to Client | REAL | LSW | 1 | per ADM100W config |  | GVL_COM.COM_<INSTANCE>.HMI_OUTPUT_L2_MAX_LOAD.Word_value[0] | Paste in INPUT_REGISTERS
|  | HMI | <INSTANCE> | ADM100W L2 Max Load | PLC to Client | REAL | MSW | 1 | per ADM100W config |  | GVL_COM.COM_<INSTANCE>.HMI_OUTPUT_L2_MAX_LOAD.Word_value[1] | Paste in INPUT_REGISTERS
|  | HMI | <INSTANCE> | ADM100W L1-L3 Voltage Phase Angle | PLC to Client | REAL | LSW | 1 | ° |  | GVL_COM.COM_<INSTANCE>.HMI_OUTPUT_L1_L3_VOLTAGE_PHASE_ANGLE.Word_value[0] | Paste in INPUT_REGISTERS
|  | HMI | <INSTANCE> | ADM100W L1-L3 Voltage Phase Angle | PLC to Client | REAL | MSW | 1 | ° |  | GVL_COM.COM_<INSTANCE>.HMI_OUTPUT_L1_L3_VOLTAGE_PHASE_ANGLE.Word_value[1] | Paste in INPUT_REGISTERS
|  | HMI | <INSTANCE> | ADM100W L3-L1 Voltage | PLC to Client | REAL | LSW | 1 | V |  | GVL_COM.COM_<INSTANCE>.HMI_OUTPUT_L3_L1_VOLTAGE.Word_value[0] | Paste in INPUT_REGISTERS
|  | HMI | <INSTANCE> | ADM100W L3-L1 Voltage | PLC to Client | REAL | MSW | 1 | V |  | GVL_COM.COM_<INSTANCE>.HMI_OUTPUT_L3_L1_VOLTAGE.Word_value[1] | Paste in INPUT_REGISTERS
|  | HMI | <INSTANCE> | ADM100W L3-N Voltage | PLC to Client | REAL | LSW | 1 | V |  | GVL_COM.COM_<INSTANCE>.HMI_OUTPUT_L3_N_VOLTAGE.Word_value[0] | Paste in INPUT_REGISTERS
|  | HMI | <INSTANCE> | ADM100W L3-N Voltage | PLC to Client | REAL | MSW | 1 | V |  | GVL_COM.COM_<INSTANCE>.HMI_OUTPUT_L3_N_VOLTAGE.Word_value[1] | Paste in INPUT_REGISTERS
|  | HMI | <INSTANCE> | ADM100W L3 Current | PLC to Client | REAL | LSW | 1 | A |  | GVL_COM.COM_<INSTANCE>.HMI_OUTPUT_L3_CURRENT.Word_value[0] | Paste in INPUT_REGISTERS
|  | HMI | <INSTANCE> | ADM100W L3 Current | PLC to Client | REAL | MSW | 1 | A |  | GVL_COM.COM_<INSTANCE>.HMI_OUTPUT_L3_CURRENT.Word_value[1] | Paste in INPUT_REGISTERS
|  | HMI | <INSTANCE> | ADM100W L3 Active Power | PLC to Client | REAL | LSW | 1 | per ADM100W config |  | GVL_COM.COM_<INSTANCE>.HMI_OUTPUT_L3_ACTIVE_POWER.Word_value[0] | Paste in INPUT_REGISTERS
|  | HMI | <INSTANCE> | ADM100W L3 Active Power | PLC to Client | REAL | MSW | 1 | per ADM100W config |  | GVL_COM.COM_<INSTANCE>.HMI_OUTPUT_L3_ACTIVE_POWER.Word_value[1] | Paste in INPUT_REGISTERS
|  | HMI | <INSTANCE> | ADM100W L3 Apparent Power | PLC to Client | REAL | LSW | 1 | per ADM100W config |  | GVL_COM.COM_<INSTANCE>.HMI_OUTPUT_L3_APPARENT_POWER.Word_value[0] | Paste in INPUT_REGISTERS
|  | HMI | <INSTANCE> | ADM100W L3 Apparent Power | PLC to Client | REAL | MSW | 1 | per ADM100W config |  | GVL_COM.COM_<INSTANCE>.HMI_OUTPUT_L3_APPARENT_POWER.Word_value[1] | Paste in INPUT_REGISTERS
|  | HMI | <INSTANCE> | ADM100W L3 Reactive Power | PLC to Client | REAL | LSW | 1 | per ADM100W config |  | GVL_COM.COM_<INSTANCE>.HMI_OUTPUT_L3_REACTIVE_POWER.Word_value[0] | Paste in INPUT_REGISTERS
|  | HMI | <INSTANCE> | ADM100W L3 Reactive Power | PLC to Client | REAL | MSW | 1 | per ADM100W config |  | GVL_COM.COM_<INSTANCE>.HMI_OUTPUT_L3_REACTIVE_POWER.Word_value[1] | Paste in INPUT_REGISTERS
|  | HMI | <INSTANCE> | ADM100W L3 Current Phase Angle | PLC to Client | REAL | LSW | 1 | ° |  | GVL_COM.COM_<INSTANCE>.HMI_OUTPUT_L3_CURRENT_PHASE_ANGLE.Word_value[0] | Paste in INPUT_REGISTERS
|  | HMI | <INSTANCE> | ADM100W L3 Current Phase Angle | PLC to Client | REAL | MSW | 1 | ° |  | GVL_COM.COM_<INSTANCE>.HMI_OUTPUT_L3_CURRENT_PHASE_ANGLE.Word_value[1] | Paste in INPUT_REGISTERS
|  | HMI | <INSTANCE> | ADM100W L3 Power Factor | PLC to Client | REAL | LSW | 1 |  |  | GVL_COM.COM_<INSTANCE>.HMI_OUTPUT_L3_POWER_FACTOR.Word_value[0] | Paste in INPUT_REGISTERS
|  | HMI | <INSTANCE> | ADM100W L3 Power Factor | PLC to Client | REAL | MSW | 1 |  |  | GVL_COM.COM_<INSTANCE>.HMI_OUTPUT_L3_POWER_FACTOR.Word_value[1] | Paste in INPUT_REGISTERS
|  | HMI | <INSTANCE> | ADM100W L3 Voltage THD | PLC to Client | REAL | LSW | 1 | % |  | GVL_COM.COM_<INSTANCE>.HMI_OUTPUT_L3_VOLTAGE_THD.Word_value[0] | Paste in INPUT_REGISTERS
|  | HMI | <INSTANCE> | ADM100W L3 Voltage THD | PLC to Client | REAL | MSW | 1 | % |  | GVL_COM.COM_<INSTANCE>.HMI_OUTPUT_L3_VOLTAGE_THD.Word_value[1] | Paste in INPUT_REGISTERS
|  | HMI | <INSTANCE> | ADM100W L3 Current THD | PLC to Client | REAL | LSW | 1 | % |  | GVL_COM.COM_<INSTANCE>.HMI_OUTPUT_L3_CURRENT_THD.Word_value[0] | Paste in INPUT_REGISTERS
|  | HMI | <INSTANCE> | ADM100W L3 Current THD | PLC to Client | REAL | MSW | 1 | % |  | GVL_COM.COM_<INSTANCE>.HMI_OUTPUT_L3_CURRENT_THD.Word_value[1] | Paste in INPUT_REGISTERS
|  | HMI | <INSTANCE> | ADM100W L3 Max Load | PLC to Client | REAL | LSW | 1 | per ADM100W config |  | GVL_COM.COM_<INSTANCE>.HMI_OUTPUT_L3_MAX_LOAD.Word_value[0] | Paste in INPUT_REGISTERS
|  | HMI | <INSTANCE> | ADM100W L3 Max Load | PLC to Client | REAL | MSW | 1 | per ADM100W config |  | GVL_COM.COM_<INSTANCE>.HMI_OUTPUT_L3_MAX_LOAD.Word_value[1] | Paste in INPUT_REGISTERS
|  | HMI | <INSTANCE> | ADM100W Internal Temperature | PLC to Client | REAL | LSW | 1 | per ADM100W config |  | GVL_COM.COM_<INSTANCE>.HMI_OUTPUT_INTERNAL_TEMPERATURE.Word_value[0] | Paste in INPUT_REGISTERS
|  | HMI | <INSTANCE> | ADM100W Internal Temperature | PLC to Client | REAL | MSW | 1 | per ADM100W config |  | GVL_COM.COM_<INSTANCE>.HMI_OUTPUT_INTERNAL_TEMPERATURE.Word_value[1] | Paste in INPUT_REGISTERS
|  | HMI | <INSTANCE> | ADM100W Active Energy | PLC to Client | REAL | LSW | 1 | per ADM100W config |  | GVL_COM.COM_<INSTANCE>.HMI_OUTPUT_ACTIVE_ENERGY.Word_value[0] | Paste in INPUT_REGISTERS
|  | HMI | <INSTANCE> | ADM100W Active Energy | PLC to Client | REAL | MSW | 1 | per ADM100W config |  | GVL_COM.COM_<INSTANCE>.HMI_OUTPUT_ACTIVE_ENERGY.Word_value[1] | Paste in INPUT_REGISTERS
|  | HMI | <INSTANCE> | ADM100W Apparent Energy | PLC to Client | REAL | LSW | 1 | per ADM100W config |  | GVL_COM.COM_<INSTANCE>.HMI_OUTPUT_APPARENT_ENERGY.Word_value[0] | Paste in INPUT_REGISTERS
|  | HMI | <INSTANCE> | ADM100W Apparent Energy | PLC to Client | REAL | MSW | 1 | per ADM100W config |  | GVL_COM.COM_<INSTANCE>.HMI_OUTPUT_APPARENT_ENERGY.Word_value[1] | Paste in INPUT_REGISTERS
|  | HMI | <INSTANCE> | ADM100W Reactive Energy | PLC to Client | REAL | LSW | 1 | per ADM100W config |  | GVL_COM.COM_<INSTANCE>.HMI_OUTPUT_REACTIVE_ENERGY.Word_value[0] | Paste in INPUT_REGISTERS
|  | HMI | <INSTANCE> | ADM100W Reactive Energy | PLC to Client | REAL | MSW | 1 | per ADM100W config |  | GVL_COM.COM_<INSTANCE>.HMI_OUTPUT_REACTIVE_ENERGY.Word_value[1] | Paste in INPUT_REGISTERS
|  | HMI | <INSTANCE> | ADM100W Total Active Power | PLC to Client | REAL | LSW | 1 | per ADM100W config |  | GVL_COM.COM_<INSTANCE>.HMI_OUTPUT_TOTAL_ACTIVE_POWER.Word_value[0] | Paste in INPUT_REGISTERS
|  | HMI | <INSTANCE> | ADM100W Total Active Power | PLC to Client | REAL | MSW | 1 | per ADM100W config |  | GVL_COM.COM_<INSTANCE>.HMI_OUTPUT_TOTAL_ACTIVE_POWER.Word_value[1] | Paste in INPUT_REGISTERS
|  | HMI | <INSTANCE> | ADM100W Total Apparent Power | PLC to Client | REAL | LSW | 1 | per ADM100W config |  | GVL_COM.COM_<INSTANCE>.HMI_OUTPUT_TOTAL_APPARENT_POWER.Word_value[0] | Paste in INPUT_REGISTERS
|  | HMI | <INSTANCE> | ADM100W Total Apparent Power | PLC to Client | REAL | MSW | 1 | per ADM100W config |  | GVL_COM.COM_<INSTANCE>.HMI_OUTPUT_TOTAL_APPARENT_POWER.Word_value[1] | Paste in INPUT_REGISTERS
|  | HMI | <INSTANCE> | ADM100W Total Reactive Power | PLC to Client | REAL | LSW | 1 | per ADM100W config |  | GVL_COM.COM_<INSTANCE>.HMI_OUTPUT_TOTAL_REACTIVE_POWER.Word_value[0] | Paste in INPUT_REGISTERS
|  | HMI | <INSTANCE> | ADM100W Total Reactive Power | PLC to Client | REAL | MSW | 1 | per ADM100W config |  | GVL_COM.COM_<INSTANCE>.HMI_OUTPUT_TOTAL_REACTIVE_POWER.Word_value[1] | Paste in INPUT_REGISTERS
|  | HMI | <INSTANCE> | ADM100W All Phase Power Factor | PLC to Client | REAL | LSW | 1 |  |  | GVL_COM.COM_<INSTANCE>.HMI_OUTPUT_ALL_PHASE_POWER_FACTOR.Word_value[0] | Paste in INPUT_REGISTERS
|  | HMI | <INSTANCE> | ADM100W All Phase Power Factor | PLC to Client | REAL | MSW | 1 |  |  | GVL_COM.COM_<INSTANCE>.HMI_OUTPUT_ALL_PHASE_POWER_FACTOR.Word_value[1] | Paste in INPUT_REGISTERS
|  | FUXA | <INSTANCE> | ADM100W Frequency | PLC to Client | REAL | LSW | 1 | Hz |  | GVL_COM.COM_<INSTANCE>.SCADA_OUTPUT_FREQUENCY.Word_value[0] | Paste in INPUT_REGISTERS
|  | FUXA | <INSTANCE> | ADM100W Frequency | PLC to Client | REAL | MSW | 1 | Hz |  | GVL_COM.COM_<INSTANCE>.SCADA_OUTPUT_FREQUENCY.Word_value[1] | Paste in INPUT_REGISTERS
|  | FUXA | <INSTANCE> | ADM100W L1-L2 Voltage | PLC to Client | REAL | LSW | 1 | V |  | GVL_COM.COM_<INSTANCE>.SCADA_OUTPUT_L1_L2_VOLTAGE.Word_value[0] | Paste in INPUT_REGISTERS
|  | FUXA | <INSTANCE> | ADM100W L1-L2 Voltage | PLC to Client | REAL | MSW | 1 | V |  | GVL_COM.COM_<INSTANCE>.SCADA_OUTPUT_L1_L2_VOLTAGE.Word_value[1] | Paste in INPUT_REGISTERS
|  | FUXA | <INSTANCE> | ADM100W L1-N Voltage | PLC to Client | REAL | LSW | 1 | V |  | GVL_COM.COM_<INSTANCE>.SCADA_OUTPUT_L1_N_VOLTAGE.Word_value[0] | Paste in INPUT_REGISTERS
|  | FUXA | <INSTANCE> | ADM100W L1-N Voltage | PLC to Client | REAL | MSW | 1 | V |  | GVL_COM.COM_<INSTANCE>.SCADA_OUTPUT_L1_N_VOLTAGE.Word_value[1] | Paste in INPUT_REGISTERS
|  | FUXA | <INSTANCE> | ADM100W L1 Current | PLC to Client | REAL | LSW | 1 | A |  | GVL_COM.COM_<INSTANCE>.SCADA_OUTPUT_L1_CURRENT.Word_value[0] | Paste in INPUT_REGISTERS
|  | FUXA | <INSTANCE> | ADM100W L1 Current | PLC to Client | REAL | MSW | 1 | A |  | GVL_COM.COM_<INSTANCE>.SCADA_OUTPUT_L1_CURRENT.Word_value[1] | Paste in INPUT_REGISTERS
|  | FUXA | <INSTANCE> | ADM100W L1 Active Power | PLC to Client | REAL | LSW | 1 | per ADM100W config |  | GVL_COM.COM_<INSTANCE>.SCADA_OUTPUT_L1_ACTIVE_POWER.Word_value[0] | Paste in INPUT_REGISTERS
|  | FUXA | <INSTANCE> | ADM100W L1 Active Power | PLC to Client | REAL | MSW | 1 | per ADM100W config |  | GVL_COM.COM_<INSTANCE>.SCADA_OUTPUT_L1_ACTIVE_POWER.Word_value[1] | Paste in INPUT_REGISTERS
|  | FUXA | <INSTANCE> | ADM100W L1 Apparent Power | PLC to Client | REAL | LSW | 1 | per ADM100W config |  | GVL_COM.COM_<INSTANCE>.SCADA_OUTPUT_L1_APPARENT_POWER.Word_value[0] | Paste in INPUT_REGISTERS
|  | FUXA | <INSTANCE> | ADM100W L1 Apparent Power | PLC to Client | REAL | MSW | 1 | per ADM100W config |  | GVL_COM.COM_<INSTANCE>.SCADA_OUTPUT_L1_APPARENT_POWER.Word_value[1] | Paste in INPUT_REGISTERS
|  | FUXA | <INSTANCE> | ADM100W L1 Reactive Power | PLC to Client | REAL | LSW | 1 | per ADM100W config |  | GVL_COM.COM_<INSTANCE>.SCADA_OUTPUT_L1_REACTIVE_POWER.Word_value[0] | Paste in INPUT_REGISTERS
|  | FUXA | <INSTANCE> | ADM100W L1 Reactive Power | PLC to Client | REAL | MSW | 1 | per ADM100W config |  | GVL_COM.COM_<INSTANCE>.SCADA_OUTPUT_L1_REACTIVE_POWER.Word_value[1] | Paste in INPUT_REGISTERS
|  | FUXA | <INSTANCE> | ADM100W L1 Current Phase Angle | PLC to Client | REAL | LSW | 1 | ° |  | GVL_COM.COM_<INSTANCE>.SCADA_OUTPUT_L1_CURRENT_PHASE_ANGLE.Word_value[0] | Paste in INPUT_REGISTERS
|  | FUXA | <INSTANCE> | ADM100W L1 Current Phase Angle | PLC to Client | REAL | MSW | 1 | ° |  | GVL_COM.COM_<INSTANCE>.SCADA_OUTPUT_L1_CURRENT_PHASE_ANGLE.Word_value[1] | Paste in INPUT_REGISTERS
|  | FUXA | <INSTANCE> | ADM100W L1 Power Factor | PLC to Client | REAL | LSW | 1 |  |  | GVL_COM.COM_<INSTANCE>.SCADA_OUTPUT_L1_POWER_FACTOR.Word_value[0] | Paste in INPUT_REGISTERS
|  | FUXA | <INSTANCE> | ADM100W L1 Power Factor | PLC to Client | REAL | MSW | 1 |  |  | GVL_COM.COM_<INSTANCE>.SCADA_OUTPUT_L1_POWER_FACTOR.Word_value[1] | Paste in INPUT_REGISTERS
|  | FUXA | <INSTANCE> | ADM100W L1 Voltage THD | PLC to Client | REAL | LSW | 1 | % |  | GVL_COM.COM_<INSTANCE>.SCADA_OUTPUT_L1_VOLTAGE_THD.Word_value[0] | Paste in INPUT_REGISTERS
|  | FUXA | <INSTANCE> | ADM100W L1 Voltage THD | PLC to Client | REAL | MSW | 1 | % |  | GVL_COM.COM_<INSTANCE>.SCADA_OUTPUT_L1_VOLTAGE_THD.Word_value[1] | Paste in INPUT_REGISTERS
|  | FUXA | <INSTANCE> | ADM100W L1 Current THD | PLC to Client | REAL | LSW | 1 | % |  | GVL_COM.COM_<INSTANCE>.SCADA_OUTPUT_L1_CURRENT_THD.Word_value[0] | Paste in INPUT_REGISTERS
|  | FUXA | <INSTANCE> | ADM100W L1 Current THD | PLC to Client | REAL | MSW | 1 | % |  | GVL_COM.COM_<INSTANCE>.SCADA_OUTPUT_L1_CURRENT_THD.Word_value[1] | Paste in INPUT_REGISTERS
|  | FUXA | <INSTANCE> | ADM100W L1 Max Load | PLC to Client | REAL | LSW | 1 | per ADM100W config |  | GVL_COM.COM_<INSTANCE>.SCADA_OUTPUT_L1_MAX_LOAD.Word_value[0] | Paste in INPUT_REGISTERS
|  | FUXA | <INSTANCE> | ADM100W L1 Max Load | PLC to Client | REAL | MSW | 1 | per ADM100W config |  | GVL_COM.COM_<INSTANCE>.SCADA_OUTPUT_L1_MAX_LOAD.Word_value[1] | Paste in INPUT_REGISTERS
|  | FUXA | <INSTANCE> | ADM100W L1-L2 Voltage Phase Angle | PLC to Client | REAL | LSW | 1 | ° |  | GVL_COM.COM_<INSTANCE>.SCADA_OUTPUT_L1_L2_VOLTAGE_PHASE_ANGLE.Word_value[0] | Paste in INPUT_REGISTERS
|  | FUXA | <INSTANCE> | ADM100W L1-L2 Voltage Phase Angle | PLC to Client | REAL | MSW | 1 | ° |  | GVL_COM.COM_<INSTANCE>.SCADA_OUTPUT_L1_L2_VOLTAGE_PHASE_ANGLE.Word_value[1] | Paste in INPUT_REGISTERS
|  | FUXA | <INSTANCE> | ADM100W L2-L3 Voltage | PLC to Client | REAL | LSW | 1 | V |  | GVL_COM.COM_<INSTANCE>.SCADA_OUTPUT_L2_L3_VOLTAGE.Word_value[0] | Paste in INPUT_REGISTERS
|  | FUXA | <INSTANCE> | ADM100W L2-L3 Voltage | PLC to Client | REAL | MSW | 1 | V |  | GVL_COM.COM_<INSTANCE>.SCADA_OUTPUT_L2_L3_VOLTAGE.Word_value[1] | Paste in INPUT_REGISTERS
|  | FUXA | <INSTANCE> | ADM100W L2-N Voltage | PLC to Client | REAL | LSW | 1 | V |  | GVL_COM.COM_<INSTANCE>.SCADA_OUTPUT_L2_N_VOLTAGE.Word_value[0] | Paste in INPUT_REGISTERS
|  | FUXA | <INSTANCE> | ADM100W L2-N Voltage | PLC to Client | REAL | MSW | 1 | V |  | GVL_COM.COM_<INSTANCE>.SCADA_OUTPUT_L2_N_VOLTAGE.Word_value[1] | Paste in INPUT_REGISTERS
|  | FUXA | <INSTANCE> | ADM100W L2 Current | PLC to Client | REAL | LSW | 1 | A |  | GVL_COM.COM_<INSTANCE>.SCADA_OUTPUT_L2_CURRENT.Word_value[0] | Paste in INPUT_REGISTERS
|  | FUXA | <INSTANCE> | ADM100W L2 Current | PLC to Client | REAL | MSW | 1 | A |  | GVL_COM.COM_<INSTANCE>.SCADA_OUTPUT_L2_CURRENT.Word_value[1] | Paste in INPUT_REGISTERS
|  | FUXA | <INSTANCE> | ADM100W L2 Active Power | PLC to Client | REAL | LSW | 1 | per ADM100W config |  | GVL_COM.COM_<INSTANCE>.SCADA_OUTPUT_L2_ACTIVE_POWER.Word_value[0] | Paste in INPUT_REGISTERS
|  | FUXA | <INSTANCE> | ADM100W L2 Active Power | PLC to Client | REAL | MSW | 1 | per ADM100W config |  | GVL_COM.COM_<INSTANCE>.SCADA_OUTPUT_L2_ACTIVE_POWER.Word_value[1] | Paste in INPUT_REGISTERS
|  | FUXA | <INSTANCE> | ADM100W L2 Apparent Power | PLC to Client | REAL | LSW | 1 | per ADM100W config |  | GVL_COM.COM_<INSTANCE>.SCADA_OUTPUT_L2_APPARENT_POWER.Word_value[0] | Paste in INPUT_REGISTERS
|  | FUXA | <INSTANCE> | ADM100W L2 Apparent Power | PLC to Client | REAL | MSW | 1 | per ADM100W config |  | GVL_COM.COM_<INSTANCE>.SCADA_OUTPUT_L2_APPARENT_POWER.Word_value[1] | Paste in INPUT_REGISTERS
|  | FUXA | <INSTANCE> | ADM100W L2 Reactive Power | PLC to Client | REAL | LSW | 1 | per ADM100W config |  | GVL_COM.COM_<INSTANCE>.SCADA_OUTPUT_L2_REACTIVE_POWER.Word_value[0] | Paste in INPUT_REGISTERS
|  | FUXA | <INSTANCE> | ADM100W L2 Reactive Power | PLC to Client | REAL | MSW | 1 | per ADM100W config |  | GVL_COM.COM_<INSTANCE>.SCADA_OUTPUT_L2_REACTIVE_POWER.Word_value[1] | Paste in INPUT_REGISTERS
|  | FUXA | <INSTANCE> | ADM100W L2 Current Phase Angle | PLC to Client | REAL | LSW | 1 | ° |  | GVL_COM.COM_<INSTANCE>.SCADA_OUTPUT_L2_CURRENT_PHASE_ANGLE.Word_value[0] | Paste in INPUT_REGISTERS
|  | FUXA | <INSTANCE> | ADM100W L2 Current Phase Angle | PLC to Client | REAL | MSW | 1 | ° |  | GVL_COM.COM_<INSTANCE>.SCADA_OUTPUT_L2_CURRENT_PHASE_ANGLE.Word_value[1] | Paste in INPUT_REGISTERS
|  | FUXA | <INSTANCE> | ADM100W L2 Power Factor | PLC to Client | REAL | LSW | 1 |  |  | GVL_COM.COM_<INSTANCE>.SCADA_OUTPUT_L2_POWER_FACTOR.Word_value[0] | Paste in INPUT_REGISTERS
|  | FUXA | <INSTANCE> | ADM100W L2 Power Factor | PLC to Client | REAL | MSW | 1 |  |  | GVL_COM.COM_<INSTANCE>.SCADA_OUTPUT_L2_POWER_FACTOR.Word_value[1] | Paste in INPUT_REGISTERS
|  | FUXA | <INSTANCE> | ADM100W L2 Voltage THD | PLC to Client | REAL | LSW | 1 | % |  | GVL_COM.COM_<INSTANCE>.SCADA_OUTPUT_L2_VOLTAGE_THD.Word_value[0] | Paste in INPUT_REGISTERS
|  | FUXA | <INSTANCE> | ADM100W L2 Voltage THD | PLC to Client | REAL | MSW | 1 | % |  | GVL_COM.COM_<INSTANCE>.SCADA_OUTPUT_L2_VOLTAGE_THD.Word_value[1] | Paste in INPUT_REGISTERS
|  | FUXA | <INSTANCE> | ADM100W L2 Current THD | PLC to Client | REAL | LSW | 1 | % |  | GVL_COM.COM_<INSTANCE>.SCADA_OUTPUT_L2_CURRENT_THD.Word_value[0] | Paste in INPUT_REGISTERS
|  | FUXA | <INSTANCE> | ADM100W L2 Current THD | PLC to Client | REAL | MSW | 1 | % |  | GVL_COM.COM_<INSTANCE>.SCADA_OUTPUT_L2_CURRENT_THD.Word_value[1] | Paste in INPUT_REGISTERS
|  | FUXA | <INSTANCE> | ADM100W L2 Max Load | PLC to Client | REAL | LSW | 1 | per ADM100W config |  | GVL_COM.COM_<INSTANCE>.SCADA_OUTPUT_L2_MAX_LOAD.Word_value[0] | Paste in INPUT_REGISTERS
|  | FUXA | <INSTANCE> | ADM100W L2 Max Load | PLC to Client | REAL | MSW | 1 | per ADM100W config |  | GVL_COM.COM_<INSTANCE>.SCADA_OUTPUT_L2_MAX_LOAD.Word_value[1] | Paste in INPUT_REGISTERS
|  | FUXA | <INSTANCE> | ADM100W L1-L3 Voltage Phase Angle | PLC to Client | REAL | LSW | 1 | ° |  | GVL_COM.COM_<INSTANCE>.SCADA_OUTPUT_L1_L3_VOLTAGE_PHASE_ANGLE.Word_value[0] | Paste in INPUT_REGISTERS
|  | FUXA | <INSTANCE> | ADM100W L1-L3 Voltage Phase Angle | PLC to Client | REAL | MSW | 1 | ° |  | GVL_COM.COM_<INSTANCE>.SCADA_OUTPUT_L1_L3_VOLTAGE_PHASE_ANGLE.Word_value[1] | Paste in INPUT_REGISTERS
|  | FUXA | <INSTANCE> | ADM100W L3-L1 Voltage | PLC to Client | REAL | LSW | 1 | V |  | GVL_COM.COM_<INSTANCE>.SCADA_OUTPUT_L3_L1_VOLTAGE.Word_value[0] | Paste in INPUT_REGISTERS
|  | FUXA | <INSTANCE> | ADM100W L3-L1 Voltage | PLC to Client | REAL | MSW | 1 | V |  | GVL_COM.COM_<INSTANCE>.SCADA_OUTPUT_L3_L1_VOLTAGE.Word_value[1] | Paste in INPUT_REGISTERS
|  | FUXA | <INSTANCE> | ADM100W L3-N Voltage | PLC to Client | REAL | LSW | 1 | V |  | GVL_COM.COM_<INSTANCE>.SCADA_OUTPUT_L3_N_VOLTAGE.Word_value[0] | Paste in INPUT_REGISTERS
|  | FUXA | <INSTANCE> | ADM100W L3-N Voltage | PLC to Client | REAL | MSW | 1 | V |  | GVL_COM.COM_<INSTANCE>.SCADA_OUTPUT_L3_N_VOLTAGE.Word_value[1] | Paste in INPUT_REGISTERS
|  | FUXA | <INSTANCE> | ADM100W L3 Current | PLC to Client | REAL | LSW | 1 | A |  | GVL_COM.COM_<INSTANCE>.SCADA_OUTPUT_L3_CURRENT.Word_value[0] | Paste in INPUT_REGISTERS
|  | FUXA | <INSTANCE> | ADM100W L3 Current | PLC to Client | REAL | MSW | 1 | A |  | GVL_COM.COM_<INSTANCE>.SCADA_OUTPUT_L3_CURRENT.Word_value[1] | Paste in INPUT_REGISTERS
|  | FUXA | <INSTANCE> | ADM100W L3 Active Power | PLC to Client | REAL | LSW | 1 | per ADM100W config |  | GVL_COM.COM_<INSTANCE>.SCADA_OUTPUT_L3_ACTIVE_POWER.Word_value[0] | Paste in INPUT_REGISTERS
|  | FUXA | <INSTANCE> | ADM100W L3 Active Power | PLC to Client | REAL | MSW | 1 | per ADM100W config |  | GVL_COM.COM_<INSTANCE>.SCADA_OUTPUT_L3_ACTIVE_POWER.Word_value[1] | Paste in INPUT_REGISTERS
|  | FUXA | <INSTANCE> | ADM100W L3 Apparent Power | PLC to Client | REAL | LSW | 1 | per ADM100W config |  | GVL_COM.COM_<INSTANCE>.SCADA_OUTPUT_L3_APPARENT_POWER.Word_value[0] | Paste in INPUT_REGISTERS
|  | FUXA | <INSTANCE> | ADM100W L3 Apparent Power | PLC to Client | REAL | MSW | 1 | per ADM100W config |  | GVL_COM.COM_<INSTANCE>.SCADA_OUTPUT_L3_APPARENT_POWER.Word_value[1] | Paste in INPUT_REGISTERS
|  | FUXA | <INSTANCE> | ADM100W L3 Reactive Power | PLC to Client | REAL | LSW | 1 | per ADM100W config |  | GVL_COM.COM_<INSTANCE>.SCADA_OUTPUT_L3_REACTIVE_POWER.Word_value[0] | Paste in INPUT_REGISTERS
|  | FUXA | <INSTANCE> | ADM100W L3 Reactive Power | PLC to Client | REAL | MSW | 1 | per ADM100W config |  | GVL_COM.COM_<INSTANCE>.SCADA_OUTPUT_L3_REACTIVE_POWER.Word_value[1] | Paste in INPUT_REGISTERS
|  | FUXA | <INSTANCE> | ADM100W L3 Current Phase Angle | PLC to Client | REAL | LSW | 1 | ° |  | GVL_COM.COM_<INSTANCE>.SCADA_OUTPUT_L3_CURRENT_PHASE_ANGLE.Word_value[0] | Paste in INPUT_REGISTERS
|  | FUXA | <INSTANCE> | ADM100W L3 Current Phase Angle | PLC to Client | REAL | MSW | 1 | ° |  | GVL_COM.COM_<INSTANCE>.SCADA_OUTPUT_L3_CURRENT_PHASE_ANGLE.Word_value[1] | Paste in INPUT_REGISTERS
|  | FUXA | <INSTANCE> | ADM100W L3 Power Factor | PLC to Client | REAL | LSW | 1 |  |  | GVL_COM.COM_<INSTANCE>.SCADA_OUTPUT_L3_POWER_FACTOR.Word_value[0] | Paste in INPUT_REGISTERS
|  | FUXA | <INSTANCE> | ADM100W L3 Power Factor | PLC to Client | REAL | MSW | 1 |  |  | GVL_COM.COM_<INSTANCE>.SCADA_OUTPUT_L3_POWER_FACTOR.Word_value[1] | Paste in INPUT_REGISTERS
|  | FUXA | <INSTANCE> | ADM100W L3 Voltage THD | PLC to Client | REAL | LSW | 1 | % |  | GVL_COM.COM_<INSTANCE>.SCADA_OUTPUT_L3_VOLTAGE_THD.Word_value[0] | Paste in INPUT_REGISTERS
|  | FUXA | <INSTANCE> | ADM100W L3 Voltage THD | PLC to Client | REAL | MSW | 1 | % |  | GVL_COM.COM_<INSTANCE>.SCADA_OUTPUT_L3_VOLTAGE_THD.Word_value[1] | Paste in INPUT_REGISTERS
|  | FUXA | <INSTANCE> | ADM100W L3 Current THD | PLC to Client | REAL | LSW | 1 | % |  | GVL_COM.COM_<INSTANCE>.SCADA_OUTPUT_L3_CURRENT_THD.Word_value[0] | Paste in INPUT_REGISTERS
|  | FUXA | <INSTANCE> | ADM100W L3 Current THD | PLC to Client | REAL | MSW | 1 | % |  | GVL_COM.COM_<INSTANCE>.SCADA_OUTPUT_L3_CURRENT_THD.Word_value[1] | Paste in INPUT_REGISTERS
|  | FUXA | <INSTANCE> | ADM100W L3 Max Load | PLC to Client | REAL | LSW | 1 | per ADM100W config |  | GVL_COM.COM_<INSTANCE>.SCADA_OUTPUT_L3_MAX_LOAD.Word_value[0] | Paste in INPUT_REGISTERS
|  | FUXA | <INSTANCE> | ADM100W L3 Max Load | PLC to Client | REAL | MSW | 1 | per ADM100W config |  | GVL_COM.COM_<INSTANCE>.SCADA_OUTPUT_L3_MAX_LOAD.Word_value[1] | Paste in INPUT_REGISTERS
|  | FUXA | <INSTANCE> | ADM100W Internal Temperature | PLC to Client | REAL | LSW | 1 | per ADM100W config |  | GVL_COM.COM_<INSTANCE>.SCADA_OUTPUT_INTERNAL_TEMPERATURE.Word_value[0] | Paste in INPUT_REGISTERS
|  | FUXA | <INSTANCE> | ADM100W Internal Temperature | PLC to Client | REAL | MSW | 1 | per ADM100W config |  | GVL_COM.COM_<INSTANCE>.SCADA_OUTPUT_INTERNAL_TEMPERATURE.Word_value[1] | Paste in INPUT_REGISTERS
|  | FUXA | <INSTANCE> | ADM100W Active Energy | PLC to Client | REAL | LSW | 1 | per ADM100W config |  | GVL_COM.COM_<INSTANCE>.SCADA_OUTPUT_ACTIVE_ENERGY.Word_value[0] | Paste in INPUT_REGISTERS
|  | FUXA | <INSTANCE> | ADM100W Active Energy | PLC to Client | REAL | MSW | 1 | per ADM100W config |  | GVL_COM.COM_<INSTANCE>.SCADA_OUTPUT_ACTIVE_ENERGY.Word_value[1] | Paste in INPUT_REGISTERS
|  | FUXA | <INSTANCE> | ADM100W Apparent Energy | PLC to Client | REAL | LSW | 1 | per ADM100W config |  | GVL_COM.COM_<INSTANCE>.SCADA_OUTPUT_APPARENT_ENERGY.Word_value[0] | Paste in INPUT_REGISTERS
|  | FUXA | <INSTANCE> | ADM100W Apparent Energy | PLC to Client | REAL | MSW | 1 | per ADM100W config |  | GVL_COM.COM_<INSTANCE>.SCADA_OUTPUT_APPARENT_ENERGY.Word_value[1] | Paste in INPUT_REGISTERS
|  | FUXA | <INSTANCE> | ADM100W Reactive Energy | PLC to Client | REAL | LSW | 1 | per ADM100W config |  | GVL_COM.COM_<INSTANCE>.SCADA_OUTPUT_REACTIVE_ENERGY.Word_value[0] | Paste in INPUT_REGISTERS
|  | FUXA | <INSTANCE> | ADM100W Reactive Energy | PLC to Client | REAL | MSW | 1 | per ADM100W config |  | GVL_COM.COM_<INSTANCE>.SCADA_OUTPUT_REACTIVE_ENERGY.Word_value[1] | Paste in INPUT_REGISTERS
|  | FUXA | <INSTANCE> | ADM100W Total Active Power | PLC to Client | REAL | LSW | 1 | per ADM100W config |  | GVL_COM.COM_<INSTANCE>.SCADA_OUTPUT_TOTAL_ACTIVE_POWER.Word_value[0] | Paste in INPUT_REGISTERS
|  | FUXA | <INSTANCE> | ADM100W Total Active Power | PLC to Client | REAL | MSW | 1 | per ADM100W config |  | GVL_COM.COM_<INSTANCE>.SCADA_OUTPUT_TOTAL_ACTIVE_POWER.Word_value[1] | Paste in INPUT_REGISTERS
|  | FUXA | <INSTANCE> | ADM100W Total Apparent Power | PLC to Client | REAL | LSW | 1 | per ADM100W config |  | GVL_COM.COM_<INSTANCE>.SCADA_OUTPUT_TOTAL_APPARENT_POWER.Word_value[0] | Paste in INPUT_REGISTERS
|  | FUXA | <INSTANCE> | ADM100W Total Apparent Power | PLC to Client | REAL | MSW | 1 | per ADM100W config |  | GVL_COM.COM_<INSTANCE>.SCADA_OUTPUT_TOTAL_APPARENT_POWER.Word_value[1] | Paste in INPUT_REGISTERS
|  | FUXA | <INSTANCE> | ADM100W Total Reactive Power | PLC to Client | REAL | LSW | 1 | per ADM100W config |  | GVL_COM.COM_<INSTANCE>.SCADA_OUTPUT_TOTAL_REACTIVE_POWER.Word_value[0] | Paste in INPUT_REGISTERS
|  | FUXA | <INSTANCE> | ADM100W Total Reactive Power | PLC to Client | REAL | MSW | 1 | per ADM100W config |  | GVL_COM.COM_<INSTANCE>.SCADA_OUTPUT_TOTAL_REACTIVE_POWER.Word_value[1] | Paste in INPUT_REGISTERS
|  | FUXA | <INSTANCE> | ADM100W All Phase Power Factor | PLC to Client | REAL | LSW | 1 |  |  | GVL_COM.COM_<INSTANCE>.SCADA_OUTPUT_ALL_PHASE_POWER_FACTOR.Word_value[0] | Paste in INPUT_REGISTERS
|  | FUXA | <INSTANCE> | ADM100W All Phase Power Factor | PLC to Client | REAL | MSW | 1 |  |  | GVL_COM.COM_<INSTANCE>.SCADA_OUTPUT_ALL_PHASE_POWER_FACTOR.Word_value[1] | Paste in INPUT_REGISTERS
Note on A1: Address in the PLC Modbus TCP server : coils and registers from 1, discrete inputs from 10001. GVL_MODBUS index = address - 1 (discrete inputs : address - 10001).
Note on B1: Address typed in the client. FUXA : discrete inputs 100001.., others = Modbus address.
Note on C1: Supervision or device that reads / writes the address. Each client has its own address range (sheet CLIENTS).
Note on D1: Instance that owns the value (GVL_COM.COM_<instance>).
Note on E1: Readable name of the value. Used as tag name in FUXA and as label in the supervisions.
Note on F1: Client to PLC : coils and holding registers written by the client. PLC to Client : discrete inputs and input registers read by the client.
Note on G1: Type of the value seen by the client. REAL uses 2 registers.
Note on H1: 32-bit value split in 2 registers : MSW = most significant word, LSW = least significant word. Empty for 16-bit and BOOL.
Note on I1: Conversion raw value -> engineering value, as written in the equipment manual. "1" = no conversion.
Note on J1: Engineering unit of the value (free text).
Note on K1: Element of GVL_MODBUS mapped in the CODESYS device I/O mapping (Modbus server or slave channel). GVL_MODBUS = exchange variables only.
Note on L1: Variable of GVL_COM copied to / from GVL_MODBUS by GFC_COM_IN / GFC_COM_OUT.
Note on M1: Free text. In TEMPLATE_TCP : sheet of MODBUS_TCP where the row goes.

## TEMPLATE_IO
Slot | Module | CODESYS device | I/O type | Channel | Tag | Description | Instance | GVL_IOMAP variable | IOMAP type | GVL_IO member | Signal | Range min | Range max | Unit | ZIPLink | Status | Comment
Note on A1: Slot of the module on the P2-11B base (1 = first slot right of the CPU).
Note on B1: Module reference installed in the slot.
Note on C1: Name of the module in the CODESYS device tree, under P2_11B (e.g. Module_2). The I/O mapping is done there.
Note on D1: DI = discrete input, DO = discrete output, AI = analog input, AO = analog output.
Note on E1: Channel number on the module (1..16 analog, 1..32 discrete).
Note on F1: Field tag of the device (P&ID / electrical drawing reference).
Note on G1: What the channel does (comment of the GVL_IO member).
Note on H1: Instance name (e.g. DIP1500_1). Must exist in the program : GVL_COM.COM_<instance>, GVL_EXC.EXC_<instance>... <INSTANCE> in a TYPE file template = placeholder.
Note on I1: Variable mapped on the channel in the CODESYS I/O mapping of the module. Empty = spare channel.
Note on J1: Type of the GVL_IOMAP variable, as given by the module mapping.
Note on K1: Member of the instance in GVL_IO (GVL_IO.IO_<instance>.<member>), copied by GFC_IO_IN / GFC_IO_OUT.
Note on L1: Electrical signal on the channel.
Note on M1: Engineering value at the low end of the signal (e.g. at 4 mA).
Note on N1: Engineering value at the high end of the signal (e.g. at 20 mA).
Note on O1: Engineering unit of the value (free text).
Note on P1: Pre-wired cable and feedthrough module used for the field wiring.
Note on Q1: State of the row. TO CHECK = value not confirmed yet.
Note on R1: Free text. Not used by the generator.

## LISTS (hidden)
IEC_DUT | VALUE_TYPE | EXCHANGE | FUNCTION | RTU_DIR | TCP_DIR | WORD | WORD_ORDER | CHANNEL | TABLE | LINE | PLC_PORT | PLC_ROLE | BAUD | PARITY | DATA_BITS | STOP_BITS | TIMEOUT | OBJ_TYPE | INSTANCE | YESNO | COPIED_BY | SLOT | MODULE | MOD_TYPE | IO_TYPE | IOMAP_TYPE | SIGNAL | ZIPLINK | IO_STATUS | RACK_STATUS | CODESYS_DEV | CLIENT | TCP_ROLE | CLIENT_ORDER | KIND | COMM | INTERFACE | READ_CH | SECTION_TCP | FC_EXC | EXC_DIR
BOOL | BOOL | Modbus TCP FUXA Coil | FC01 Read Coils | Equipment to PLC | Client to PLC | MSW | ABCD (MSW first) | Read, cyclic | Coil | RTU_1 | RS-232/485 4-pin | Master | 1200 | None | 7 | 1 | 100 | ADM100W | ADM100W_1 | Yes | GFC_EXC_IN | 1 | P2-16AD-1 | AI | DI | BOOL | 24 VDC | ZL-CBL40-2 / ZL-RTB40-1 | Used | Installed | Module | FUXA | PLC = server | CDAB (Float32MLE) | Equipment | Modbus RTU | RS-485 | Cyclic | COILS | FC_EXC_UPI_LOCAL_FUXA_ADM100W | A -> B
BYTE | WORD | Modbus TCP FUXA DI | FC02 Read Discrete Inputs | PLC to Equipment | PLC to Client | LSW | CDAB (LSW first) | Write, cyclic | DI | RTU_2 | RS-232/485 RJ12 | Slave | 2400 | Even | 8 | 2 | 200 | DOSENSOR | DOSENSOR_1 | No | GFC_EXC_OUT | 2 | P2-16AD-2 | AO | DO | WORD | 4-20 mA | ZL-P2-CBL24-2 / ZL-RTB20-1 | Spare | Empty | Module_1 | HMI | PLC = client | CDAB, confirmed on the PV800 | Functional unit (UPI) | Modbus TCP | RS-232 | Rising edge | DISCRETE_INPUTS | FC_EXC_UPI_LOCAL_HMI_ADM100W | B -> A
WORD | INT | Modbus TCP FUXA IR | FC03 Read Holding Registers |  |  |  | BADC (byte swap) | Read, rising edge | IR | RTU_3 | TO CHECK |  | 4800 | Odd | TO CHECK | TO CHECK | 500 | DIP1500 | DIP1500_1 |  |  | 3 | P2-16DA-1 | DI | AI | DWORD | 0-20 mA |  | Reserved | Planned | Module_2 | WEBVISU |  | ABCD (Float32) |  | EtherNet/IP |  | Application | INPUT_REGISTERS | FC_EXC_UPI_LOCAL_WEBVISU_ADM100W
DWORD | UINT | Modbus TCP FUXA HR | FC04 Read Input Registers |  |  |  | DCBA (byte and word swap) | Write, rising edge of COM_OUTPUT_CMD_TRIGGER | HR |  |  |  | 9600 | TO CHECK |  |  | 1000 | UPI_LOCAL_FUXA | UPI_LOCAL_FUXA |  |  | 4 | P2-16DA-2 | DO | AO | INT | 0-10 V |  | TO CHECK | TO CHECK | Module_3 |  |  | TO CHECK |  | Wired I/O |  |  | HOLDING_REGISTERS | FC_EXC_UPI_LOCAL_FUXA_DOSENSOR
LWORD | DINT | Modbus TCP HMI Coil | FC05 Write Single Coil |  |  |  |  | Write, rising edge of COM_OUTPUT_CONFIG_TRIGGER |  |  |  |  | 19200 |  |  |  | 2000 | UPI_LOCAL_HMI | UPI_LOCAL_HMI |  |  | 5 | P2-08AD-1 | EMPTY |  | DINT | +/-10 V |  |  |  | Module_4 |  |  |  |  | None |  |  |  | FC_EXC_UPI_LOCAL_HMI_DOSENSOR
SINT | UDINT | Modbus TCP HMI DI | FC06 Write Single Register |  |  |  |  | Read, application |  |  |  |  | 38400 |  |  |  | TO CHECK | UPI_LOCAL_WEBVISU | UPI_LOCAL_WEBVISU |  |  | 6 | P2-08DA-1 |  |  | UINT | Dry contact |  |  |  | Module_5 | [8 empty] | FC_EXC_UPI_LOCAL_WEBVISU_DOSENSOR
INT | REAL | Modbus TCP HMI IR | FC15 Write Multiple Coils |  |  |  |  | Write, application |  |  |  |  | 57600 | [5 empty] | <INSTANCE> |  |  | 7 | P2-32ND3-1 |  |  | UDINT |  |  |  |  | Module_6 | [8 empty] | FC_EXC_UPI_LOCAL_FUXA_DIP1500
DINT | UDINT (time mode) / REAL (volume mode) | Modbus TCP HMI HR | FC16 Write Multiple Registers |  |  |  |  | TO CHECK |  |  |  |  | 115200 | [5 empty] | <INSTANCE_B> |  |  | 8 | P2-16ND3 |  |  | REAL |  |  |  |  | Module_7 | [8 empty] | FC_EXC_UPI_LOCAL_HMI_DIP1500
LINT |  | WebVisu (direct variable access) | FC23 Read/Write Multiple Registers | [9 empty] | TO CHECK | [8 empty] | 9 | P2-32NE3 | [7 empty] | Module_8 | [8 empty] | FC_EXC_UPI_LOCAL_WEBVISU_DIP1500
USINT |  | Modbus RTU (see RTU tables) | [19 empty] | 10 | P2-32TD1P | [7 empty] | Module_9
UINT |  | Modbus RTU write trigger (slave I/O mapping) | [19 empty] | 11 | P2-32TD2P | [7 empty] | Module_10
UDINT |  | Physical I/O (GVL_IOMAP, GFC_IO) | [20 empty] | P2-16TD2P
ULINT |  | Exchange (GFC_EXC) | [20 empty] | P2-08TRS
REAL |  | Persistent parameter (GVL_PA) | [20 empty] | P2-FILL
LREAL
TIME
STRING
DUT_Union_Real_Word
TON
TOF
TP
R_TRIG
F_TRIG
ARRAY[0..1] OF WORD
ARRAY[0..7] OF BOOL